**ASSAM ELECTRICITY GRID CORPORATION LIMITED**

Regd. Office:1st floor, Bijulee Bhawan, Paltanbazar, Guwahati-781001

CIN: U40101 AS2003SGC007238

Phone:0361-2739520/Fax:0361-2739513 web:www.aegcl.co.in

****

**Bidding Document**

**For**

**Procurement of 01 No. of 145kV SF6 Circuit breaker set (Gang Operated: CGL make) each for 132kV Nazira GSS Division and 220kV Mariani GSS Division.**

**DEPUTY GENERAL MANAGER**

**Jorhat T&T CIRCLE**

**AEGCL, Jorhat-785007**

**Tender Cost: ₹1000.00**

 **EMD: ₹40,000.00**

**BID NO: AEGCL/DGM/TTC/JRT/O&M/T-31/2025/1877 Date:05.02.2025**

For & on behalf of the **Managing Director, AEGCL, the Deputy General Manager, T&T Circle, AEGCL,Garmur,Jorhat-07** invites tenders in prescribed form, from reputed Firms/Contractors/Manufacturers with sound technical and financial capabilities for the following work. A single stage two envelope procedure (**Techno-Commercial and Price Bid**) will be adopted for this tender.

|  |  |  |  |
| --- | --- | --- | --- |
| **Sl. No.** | **Name of work** | **Estimated Cost****In INR** | **Time****of****completion****In Days** |
| 1 | **Procurement of 01 No. of 145kV SF6 Circuit breaker set (Gang Operated: CGL make) each for 132kV Nazira GSS Division and 220kV Mariani GSS Division.** | **19,76,500.00** | **06 (Six ) months from the date of approval of drawings.** |

|  |  |  |
| --- | --- | --- |
| **1.0** | **Cost of Bidding Document:** |  |
|  | Bidder must pay Non-Refundable tender document cost of **Rs.1000.00 (Rupees One Thousand) only in the form of A/C payee Demand draft (Non-refundable) pledged in favour of MD, AEGCL, Bijulee Bhawan, Paltanbazar, Guwahati-1, payable at Guwahati**.  |
| **2.0** | **Bidding Address:** |  |
| 2.1 | Tender papers can be purchased on application in plain paper from the **Deputy General Manager, T&T Circle, AEGCL, Garmur,Jorhat-07.****Key Dates: -**1. Bid Document available date: **12:00 hrs of 10.02.2025**
2. Bid Submission Start Time & date: **12:00 hrs of 10.02.2025**
3. Bid Submission end time & date: **12:00hrs of 03.03.2025**
4. Techno-Commercial Bid Opening time: **14:30hrs of 03.03.2025**
 |
| **3.0** | **Validity of Bids and Bids Prices:** |  |
| 3.1 | Bids shall remain valid for the period of 180 days after the bid submission deadline date prescribed by AEGCL. In exceptional circumstances, prior to the expiration of the bid validity period, AEGCL may request Bidders to extend the period of validity of their bids. The request and the responses shall be made in writing. If a bid security shall also be extended for a corresponding period.  |
| 3.2 | Bidder may refuse the request without forfeiting its bid security. A Bidder granting the request shall not be required or permitted to modify its bid. |
| 3.3 | Bidders shall quote for the entire scope of supply and services on a “single responsibility” basis such that the total bid price covers all the Supplier’s obligations mentioned in or to be reasonably inferred from the bidding document in respect of the design, manufacture, including procurement, delivery, and completion of the entire scope. |
| 3.4 | Bidders shall give a breakdown of the prices in the manner and detail called for in the Price Schedules.  |
| **4.0** | **Bid Security:** |
| 4.1 | All bids must be accompanied by a bid security amounting to **Rs. 40,000.00**(Rupees Forty Thousand)only in the form of Bank Guarantee/Demand Draft from any Nationalized Bank payable at Guwahati in favour of **MD**,**AEGCL, Bijulee Bhawan, Paltanbazar, Guwahati-01.** |
| 4.2 | If a bid security is specified, any bid not complying then his bid shall be rejected by the Employer as non-responsive.  |
| 4.3 | The bid security of the successful Bidder shall be returned as promptly as possible once the successful Bidder has signed the Contract and furnished the required performance security.  |
| 4.4 | The bid security of unsuccessful Bidders shall be returned as promptly as possible upon the successful Bidder ‘s furnishing of the performance security. |
| 4.5 | The bid security may be forfeited:1. if a Bidder withdraws its bid during the period of bid validity specified by the Bidder.
2. if the successful Bidder fails to:

(i) sign the Contract with in the specified period.(ii) furnish a performance security within 15 (fifteen) days’ time.  |
| 4.6 | The Bid Security of a JV shall be in the name of the JV that submits the bid. If the JV has not been legally constituted at the time of bidding, the Bid Security shall be in the names of all future partners as named in the letter of intent. |
| 4.7 | If a bid securing declaration is not executed in accordance with the above, AEGCL will declare the Bidder ineligible to be awarded a contract by the AEGCL for the period of time stated in the Form of Bid Securing Declaration. |
| **5.0** | **Format and Signing of Bid:** |
| 5.1 | The Bidder shall prepare one original of the Technical Bid and one original of the Price Bid comprising the Bid and clearly mark it ―ORIGINAL - TECHNICAL BID and ―ORIGINAL - PRICE BID. In addition, the Bidder shall submit three copies of the bid, in the number specified and clearly mark each of them ―COPY. In the event of any discrepancy between the original and the copies, the original shall prevail bid. |
| 5.2 | The original and all copies of the Bid shall be typed or written in indelible ink and shall be signed by a person duly authorized to sign on behalf of the Bidder. This authorization shall consist of a written confirmation as specified in the Bid Document and shall be attached to the bid. The name and position held by each person signing the authorization must be typed or printed below the signature. All pages of the bid where entries or amendments have been made shall be signed or initialed by the person signing the bid. |
| 5.3 | A bid submitted by a JV shall be signed to be legally binding on all partners. |
| 5.4 | Any interlineations, erasures, or overwriting shall be valid only if they are signed or initialed by the person signing the bid. |
| **6.0** | **Submission and Opening of Bids:** |
| **6.1** | **Submission, Sealing and Marking of Bids:** |
| 6.1.1 | Bidders may submit their bids by mail or by hand. When so specified in the Bid Document, bidders shall have the option of submitting their bids electronically. Procedures for submission, sealing and marking are as follows:Bidders submitting bids by mail or by hand shall enclose the original and each copy of the Bid, including alternative bids, if permitted in accordance with above, in separate sealed envelopes, duly marking the envelopes as ―ORIGINAL and ―COPY. These envelopes containing the original and the copies shall then be enclosed in one single envelope.  |
| 6.1.2 | The inner and outer envelopes shall:1. bear the name and address of the Bidder;
2. be addressed to the Bidding Authority.
3. bear the specific identification of this bidding process indicated in the Bid Document
 |
| 6.1.3 | The outer envelopes and the inner envelopes containing the Technical Bid shall bear a warning not to open before the time and date for the opening of Technical Bid. |
| 6.1.4 | The inner envelopes containing the Price Bid shall bear a warning not to open until advised by the AEGCL. |
| 6.1.5 | If all envelopes are not sealed and marked as required, the Employer will assume no responsibility for the misplacement or premature opening of the bid. |
| **6.2** | AEGCL may, at its discretion, extend the deadline for the submission of bids by amending the Bidding Document, in which case all rights and obligations of the AEGCL and Bidders previously subject to the deadline shall thereafter be subject to the deadline as extended. |
| **7.0** | **Eligible Bidders:** |
| 7.1 | A Bidder may be a private entity or a government-owned entity or any combination of such entities with the intent to enter into an agreement supported by a letter of intent or under an existing agreement in the form of a joint venture, consortium, or association (JV). In the case of a JV:1. all partners shall be jointly and severally liable, and
2. the JV shall nominate a Representative who shall have the authority to conduct all business for and on behalf of all the partners of the JV during the bidding process and, in the event the JV is awarded the Contract, during contract execution.
 |
| 7.2 | A Bidder, and all partners constituting the Bidder, shall have Indian nationality. A Bidder shall be deemed to have the nationality of a country if the Bidder is a national or is constituted, incorporated, or registered and operates in conformity with the provisions of the laws of Republic of India. This criterion shall also apply to the determination of the nationality of proposed subcontractors or suppliers for any part of the Contract including related services. |
| 7.3 | AEGCL considers a conflict **of interest** to be a situation in which a party has interests that could improperly influence that party ‘s performance of official duties or responsibilities, contractual obligations, or compliance with applicable laws and regulations, and that such conflict of interest may contribute to or constitute a prohibited practice under Anticorruption Policy of Government of India and Government of Assam. In pursuance Anticorruption Policy‘s requirement that Employer as well as bidders, suppliers, and contractors observe the highest standard of ethics. AEGCL will take appropriate actions if it determines that a conflict of interest has flawed the integrity of any procurement process. Consequently, all Bidders found to have a conflict of interest shall be disqualified. A Bidder may be in a conflict of interest with one or more parties in this bidding process if, including but not limited to:(a). they have controlling partners in common; or(b). they receive or have received any direct or indirect subsidy from any of them; or(c). they have the same legal representative for purposes of this bid; or(d). they have a relationship with each other, directly or through common third parties, that puts them in a position to have access to information about or influence on the bid of another Bidder, or influence the decisions of the Employer regarding this bidding process; or(e). a Bidder participates in more than one bid in this bidding process. Participation by a Bidder in more than one Bid will result in the disqualification of all Bids in which it is involved. However, this does not limit the inclusion of the same subcontractor, not otherwise participating as a Bidder, in more than one bid; or (f). a Bidder or any of its affiliates participated as a consultant in the preparation of the design or technical specifications of the plant and services that are the subject of the bid. |
| 7.4 | A firm that is under a declaration of ineligibility by the AEGCL or any Government Entity or PSU at the date of the deadline for bid submission or thereafter i.e., on or before contract signing date shall be disqualified.  |
| 7.5 | Bidders shall provide such evidence of their continued eligibility satisfactory to the AEGCL, as the Employer shall reasonably request. |
| 7.6 | In case a prequalification process has been conducted prior to the bidding process, this bidding is open only to prequalified Bidders. |
| **8.0** | **Financial Capability:** |
| 8.1 | Bidder will require to submit along with the bid the audited balance sheets and other legal financial statements acceptable to AEGCL, for the last 3 (three) years to demonstrate the current soundness of the Bidders financial position and its prospective long-term profitability. As a minimum, an Applicant‘s net worth calculated as the difference between total assets and total liabilities should be positive. |
| 8.2 | ***Average Annual Turnover***: Minimum average annual turnover **INR 6,00,000.00**calculated as total certified payments received for contracts in progress or completed, within the last 3 (Three) Years. |
| 8.3 | ***Financial Resources***: Bidder need to demonstrate access to, or availability of, financial resources such as liquid assets, unencumbered real assets, lines of credit, and other financial means, other than any contractual advance payments to meet: (1) the following cash-flow requirement, INR **6,00,000.00**and(2) the overall cash flow requirements for this contract and its current works commitment. |
| **9.0** | **Experience:** |
| 9.1 | Experience on similar nature of works under contracts in the role of manufacturers, contractor, subcontractor, or management contractor for at least the last 7(Seven) years prior to the bid submission deadline. Bidder may be manufacturer of the offered products or a firm/company having authorization from a manufacturer. In case the bidder is not a manufacturer of the offered products, bidder must submit manufacturer’s authorization |
| 9.2 | Participation as manufacturer, contractor Experience having successfully completed similar works during last 7 years ending last day of the month before the one in which applications are invited should be either of the following:1. Three (3) similar completed works costing not less than **6,00,000.00**
2. Two (2) similar completed works costing not less than **9,90,000.00**
3. One (1) similar completed works costing not less than **15,90,000.00**
 |
|  |  |
| 9.3 | The Bidder must have experience of executing work of similar nature previously. The bidder must submit experience and completion certificate for scrutiny by AEGCL**.** Each of such project/ works should consist of completion certificate as per Clause 9.1. |
| **10.0** | **Evaluation Criteria:** |
| 10.1 | Evaluation will be done on the basis of *Bid Clause***. 6.0**, Eligibility, Cl. No. 7**.**0, Financial Capability, Cl. No. **8.0**.,, Experience and in accordance with the **Annexure I** to be duly filled in, signed, and submitted by the bidder. |
| 10.2 | Price Bid of only **Responsive Techno-Commercial Bidders** will be opened.  |
| 10.3 | **Arithmetical Error,** if observed while in Price Bid evaluation, same will only be corrected. |
| 10.4 | **Any post bid correction request will NOT BE ENTERTAINED.** |
| 10.510.6  | **Price Bid Envelope of the Non-responsive Techno Commercial Bidders will be returned** to the respective bidders against submission of a written request by the bidder.The following methodology will be practiced for identification and treatment of the Abnormally Low Bids (ALB) in this tender process of AEGCL: (i) Absolute Approach is to be considered when there is fewer than five substantially responsive bidders and if the bid price is 20% or more below AEGCL’s cost estimate then AEGCL’s tender evaluation committee should clarify the Bid price with the bidder to determine whether the Bid isAbnormally low. (ii) Relative approach is to be considered when there are at least 5(five) nos. of substantially responsive bids and the lowest bid price is 20% or more below AEGCL’s cost estimate. In this approach, first the Average bid price is determined and then by deducting the standard deviation from the Average bid price, potentially ALB may be determined. (iii) In case of an ALB, the tender evaluation committee/appropriate authority of the respective tenders shall undertake the following three stage review process which is as below:* To identify ALB as per the steps mentioned in SI no. 10.6.(i) and 10.6.(ii), whichever is applicable.
* To seek and analyses the clarifications from the abnormally low Bidder in terms of resource inputs and pricing, including overheads, contingencies, and profit margins. In that respect, the committee may refer to guideline of World Bank, AIIB, ADB etc. prescribed for ALB.
* To decide whether to accept or reject the bid.
* On acceptance of the bid, whether Additional Performance Security is to be imposed on the bidder supplemented by adequate justification.

 (iv) In case of acceptance of ALB with Additional Performance Security:* If any abnormally low bid is accepted with additional performance security, it is to be noted that the total performance security should not exceed 20% of the total contract value.
* The additional performance security shall be treated as part of the original performance security and shall be valid for a period similar to that applicable for defect liability period of the contract.
* Non submission of the additional performance security shall constitute sufficient ground for rejection of the bid and similar assessment shall then be initiated for next ranked bidder if that bidder is also identified as ALB.
 |
| **11.0** | **Late Bid:** |
| 11.1 | Any bid submitted ***after the due date and time*** will be rejected without any prejudice. |
| 11.2 | AEGCL will not be responsible for any Postal and/or Courier Delay in delivering the bid. The same received after the scheduled closing date and time will be rejected without any prejudice. |
| 11.3 | Bidding through EMAIL WILL NOT BE ACCEPTED. |
| **12.0** | **Clarification:** |
| 12.1 | A prospective Bidder requiring any clarification of the Bidding Document shall contact the AEGCL in writing at the AEGCL ‘s address indicated in the BDS or raise his enquiries prior to 7 (seven) days of closing of the bid. The Employer will respond to any request for clarification, provided that such request is received no later than seven (7) days prior to the deadline for submission of bids. The AEGCL ‘s response shall be in writing with copies to all Bidders who have acquired the Bidding Document including a description of the inquiry but without identifying its source. Should AEGCL deem it necessary to amend the Bidding Document as a result of a request for clarification, it shall do so.  |
|  |  |
|  |  |
|  |  |
|  |  |
|  |  |
|  |  |
| **13.0** | **Amendment of Bidding Document:** |
| 13.1 | At any time prior to the deadline for submission of bids, the Employer may amend the Bidding Document by issuing addenda. |
| 13.2 | Any addendum issued shall be part of the Bidding Document and shall be communicated in writing to all who have obtained the Bidding Document from AEGCL. |
| 13.3 | To give prospective Bidders reasonable time in which to take an addendum into account in preparing their bids, AEGCL may, at its discretion, extend the deadline for the submission of bids. |
| **14.0** | **Preparation of Bids by the Bidders:** |
| 14.1 | **Cost of bidding:** The Bidder shall bear all costs associated with the preparation and submission of its Bid, and AEGCL shall not be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process. |
| 14.2 | **Language of Bid:** The Bid, as well as all correspondence and documents relating to the bid exchanged by the Bidder and AEGCL, shall be written in the English language.  |
| **14.3** | **Bid Prices and Discounts:** |
| 14.3.1 | Unless otherwise specified in the Bid Document and/or AEGCL’s Requirements, bidders shall quote for the entire plant and services on a ―single responsibility basis such that the total bid price covers all the Contractor ‘s obligations mentioned in or to be reasonably inferred from the bidding document in respect of the including procurement and subcontracting (if any), delivery, construction, installation, and completion of the Work. This includes all requirements under the Contractor ‘s responsibilities for completing the work and where so required by the bidding document, the acquisition of all permits, approvals, and licenses, etc.; the operation, maintenance and training services and such other items and services as may be specified in the Bidding Document, all in accordance with the requirements of the General Conditions. Items against which no price is entered by the Bidder will not be paid for by the Employer when executed and shall be deemed to be covered by the prices for other items. |
| 14.3.2 | Bidders are required to quote the price for the commercial, contractual, and technical obligations outlined in the bidding document. If a Bidder wishes to make a deviation, such deviation shall be listed. The Bidder shall also provide the additional price if any, for withdrawal of the deviation. |
|  |  |
| 14.3.3 | Bidders shall give a breakdown of the prices in the manner and detail called for in the Price Schedules. Where no different Price Schedules are included in the Bidding Document, bidders shall present their prices in the following manner: (a)Separate numbered Schedules shall be used for each of the following elements.(I) The total amount from each Schedule shall be summarized in a Grand Summary giving the total bid price(s) to be considered.  |
| 14.3.4 | The price of the work shall be quoted as the Base Price or EXW Price |
| 14.3.5 | Sales Tax, GST, and all other taxes (as applicable) payable on the work should be indicated separately. In case of failure to indicate so AEGCL will consider such taxes are included in the Offered Price.  |
| 14.3.6 | Whenever forest produces like sand, stone, timbers etc. are used in the work the contractor must furnish documentary proof that requisite royalty on such produces has been paid to the concerned Department. |
| 14.3.7 | When the work being “work contract” which is one and individual and which involves no separate contract for the sale of materials, the contractor shall have not been entitled to get any VAT and or any other taxes, levies reimbursed from the AEGCL for the supply of the materials. |
| 14.3.8 | Taxes like work contract, income tax etc. which need to be deducted at source as per the prevailing law of the land, will be deducted at source.  |
| 14.3.9 | **The Prices shall be FIXED and FIRM:** The Bided Price should on Fixed Price basis, prices quoted by the Bidder shall be fixed during the Bidder ‘s performance of the contract and not subject to variation on any account. A bid submitted with an adjustable price quotation will be treated as non-responsive and rejected. |
| **15.0** | **Additional Requirements:** |
|  |  |
| 15.3.1 | Bidders(s) knowledge from actual personal investigation of the resources of the region or District (S) in which he/they offers the work. |
| 15.3.2 | The Bidder shall furnish copy of their PAN Card. The card must be in the name of firm, in case the tenderer is a partnership Firm. |
| 15.3.3 | In case the tenderer is a partnership Firm, the work experience, solvency and turn over shall be in the name of partnership Firm only. |
| 15.3.4 | GST registration No., Latest Bank solvency  |
| 15.3.5 | Registered Power of attorney, if any. |
| 15.3.6 | I T Return for last three Years |
| 15.3.7 | Audited Balance Sheet for last three years |
| 15.3.8 | All other information and documents such as Guaranteed and Technical Particulars, type test reports, drawings etc., as required in the Technical Specification |
| 15.3.9 | In case the bidder is not a manufacturer of the offered products, bidder must submit manufacturer’s authorization |
| **16.0** | **Negotiation with successful bidder:** |
|  | The AEGCL reserve the right to negotiate with lowest who should be lowest, valid, eligible, and technically acceptable tenderer considered for award of contract directly if the rates were not unreasonably high. |
| **17.0** | **TECHNICAL REQUIREMENTS** |
| 17.1 | **Intent of specification** |
|  | This section of the specification deals with the technical information & criteria for **Procurement of 01 No. of 145kV SF6 Circuit breaker set (Gang Operated: CGL make) each for 132kV Nazira GSS Division and 220kV Mariani GSS Division.** The Contractor's proposal shall be based on the use of materials complying fully with the requirements specified herein. |
| **18.0** | **Scope**The major scopes of work are as follows: -a) Design, Supply, delivery of 2 nos. of 132kV SF6 Circuit breaker set as mentioned in the bidb) Transportation and movement of supplied materials up to the site and arrangements of any permits required for transportation of supplied materials. However, AEGCL shall assist as far as practicable in the process.d) Transit insurance shall be in the scope of the contractor. The works to be executed shall be as per the items mentioned in the BOQ and as per the directions of the site engineer. |
| **19.0** | **Contractor to inform himself fully** |
| 19.1 | The Contractor should ensure that he has examined the General Conditions, qualifying criteria, Specifications and Schedules and has satisfied himself as to all the conditions and circumstances affecting the contract price and fixed his price according to his own views on these matters and acknowledge that no additional allowances except as otherwise provided therein will be levied. |
| 19.2 | The Employer shall not be responsible for any misunderstanding or incorrect information obtained by the Contractor other than information given to the Contractor in writing by the Purchaser |
| **20.0** | **Conformity with Indian Electricity rules & other local regulations:** |
| 20.1 | The Contractor shall note that all substation works shall comply with the latest provisions of Indian Electricity Rules and with any other regulations. Local authorities concerned in the administration of the rules and regulation relating to such works shall be consulted, if necessary, in regard to the rules and regulations that may be applicable. |
| 20.2 | The materials covered by this specification shall, unless otherwise stated be designed, constructed, and tested in accordance with the latest revisions of relevant Indian Standards and shall conform to the regulations of local statutory authorities. |
| 20.3 | The Contractor shall also comply with the Minimum Wages Act 1948 and the payment of Wages Act (both. Of the Government of India and State of Assam) and the rules made there under in respect of any employee or workman employed or engaged by him or his Sub-Contractor. |
| 20.4 | All registration and statutory inspection fees, if any, in respect of his work pursuant to this Contract shall be to the account of the Contractor. However, any registration, statutory inspection fees lawfully payable under the provisions of the statutory laws and its amendments from time to time during erection in respect of the Substation Works, ultimately to be owned by the Employer, shall be to the account of the Employer. Should any such inspection or registration need to be re-arranged due to the fault of the Contractor or his Sub-Contractor, the additional fees to such inspection and/or registration shall be borne by the Contractor. |
| 20.5 | In case of any conflict between the standards and this specification, this specification shall govern. |
| **21.0** | **Drawing and Documents** |
| 21.1 | All necessary drawings and documents required for completion of the project is to be submitted by the contractor for approval. The drawings provided with bid (if any) are for indicative purpose only and fresh drawings are to be prepared by the contractor as per actual site condition after survey. The drawings and documents are to be approved by AEGCL. |
| **22.0** | **Employer Supervision**  |
| 22.1 | The scope of the duties of the Employer, pursuant to the contract, will include but not be limited to the following.1. Witness or authorize his representative to witness works at site.
2. Inspect, accept, or reject any material and work under the Contract.
3. Issue certificate of acceptance and/or progressive payment and final payment certificate.
4. Review and suggest modification and improvement in completion schedules from time to time.
5. Issue completion certificate.
 |
|  | **23. Packing:**  |
|  | All the materials shall be suitably protected, coated, covered, or boxed and crated to prevent damage or deterioration during transit, handling, and storage at Site till the time of erection. The Supplier shall be responsible for any loss or damage during transportation, handling, and storage due to improper packing. |
|  | The Supplier shall include and provide for securely protecting and packing the materials to avoid loss or damage during transport by air, sea, rail, and road. |
|  | All packing shall allow for easy removal and checking at site. Wherever necessary, proper arrangement for attaching slings for lifting shall be provided. All packages shall be clearly marked for with signs showing 'up' and 'down' on the sides of boxes, and handling and unpacking instructions as considered necessary. Special precaution shall be taken to prevent rusting of steel and iron parts during transit by sea. |
|  | The cases containing easily damageable material shall be very carefully packed and marked with appropriate caution symbols, i.e., fragile, handle with care, use no hook etc. wherever applicable. |
|  | Each package shall be legibly marked by the-Supplier at his expenses showing the details such as description and quantity of contents, the name of the consignee and address, the gross and net weights of the package, the name of the Supplier etc. |
|  | **24. Materials handling and storage:** |
|  | (a) All the supplies under the Contract as well as Employer supplied items (if any) arriving at site shall be promptly received, unloaded, and transported and stored in the stores by the Contractor.(b) Contractor shall be responsible for examining all the shipment and notify the Employer immediately of any damage, shortage, discrepancy etc. for the purpose of Employer's information only. The Contractor shall submit to the Employer every week a report detailing all the receipts during the week. However, the Contractor shall be solely responsible for any shortages or damages in transit, handling and/or in storage and erection at site. Any demurrage, and other such charges claimed by the transporters, railways etc., shall be to the account of the Contractor.(c) The Contractor shall maintain an accurate and exhaustive record-detailing out the list of all items received by him for the purpose of erection and keep such record open for the inspection of the Employer.(d) All items shall be handled very carefully to prevent any damage or loss. The materials stored shall be properly protected to prevent damage. The materials from the store shall be moved to the actual location at the appropriate time to avoid damage of such materials at Site.(e) All the materials stored in the open or dusty location must be covered with suitable weatherproof and flameproof covering material wherever applicable.(f) The Contractor shall be responsible for making suitable indoor storage facilities, to store all items/materials, which require indoor storage.(g) The Contractor shall have total responsibility for all equipment and materials in his custody, stored, loose, semi-assembled and/or erected by him at site. The contractor shall make suitable security arrangements including employment of security personnel to ensure the protection of all materials, equipment and works from theft, fire, pilferage and any other damages and loss. (h) The Employer will verify the storage facilities arranged by the contractor and dispatch clearance will be provided only after Employer is satisfied.1. **TECHNICAL SPECIFICATIONS OF 1 NO. OF 132KV SF6 CIRCUIT BREAKER**

**25.1General Arrangement**1. The circuit breaker shall be of three phase unit (gang operated) outdoor, single pressure puffer type. The operating mechanism shall be electrically and mechanically trip/free with anti pumping facility suitable for remote electrical closing, tripping as well as local Operation facility as specified. The CBs are meant for installation with Transformers LV side & bus section. 2. The circuit breaker shall be so designed to withstand the effects of temperature, wind load, short circuit conditions and other adverse conditions. 3. The circuit breaker shall be capable of switching transformer-magnetizing currents and shall be restrict - free.4. All similar parts, particularly removable ones, shall be interchangeable with one another. 5. All cable ferrules, lugs, tags, etc. required for cabling from equipment control cabinet/operating mechanism to the central control cabinet of the breaker shall be supplied loose as per approved schematics. 6. The SF6 breaker shall be designed to ensure that condensation of moisture is controlled by proper selection of organic insulating materials having low moisture absorbing characteristics. 7. The support structure of circuit breaker shall be hot dip galvanized. Sufficient galvanizing thickness shall be achieved with 615 gm/m². All other parts shall be painted as per painting specification enclosed separately. * + 1. **OPERATING MECHANISM**
1. A power spring operated mechanism for closing and tripping shall be provided in the breaker control cabinet. This device shall be so interlocked that while it is under maintenance, the breaker cannot be operated from remote. A slow acting, manually operated device shall be provided for inspection and maintenance purposes.
2. Circuit breaker operating mechanism shall be capable of storing energy for atleast two complete closing and tripping operations.
3. Each mechanism shall have an operation counter.
4. The operating mechanism shall be mounted and enclosed in a weather proof, vermin-proof, sheet steel cabinet conforming to IP: 55 degree of protection. Sheet steel thickness shall be as specified in data sheet. The cabinet shall also house relays, control and auxiliary equipment of each breaker and provision for terminating all control, alarm and auxiliary circuits. It shall be provided with hinged doors with provision for locking and removable gland plates to be drilled at site. Inspection window shall be provided for observation of the instruments without opening the cabinet. It shall be mounted so as to provide convenient access from ground level.
5. The cabinet shall be fitted with a thermostatically controlled anti-condensation heater, a 15A, 1 phase, 5 pin socket outlet with switch and a cubicle illuminating lamp suitable for operation on 240 V AC 50Hz supply.
6. Circuit breakers shall feature high repeatability of absolute closing time over a wide range of parameters (ambient temperature, pneumatic pressure, control voltages, etc).
7. Main poles shall operate simultaneously. There shall be no objectionable rebound and the mechanism shall not require any critical adjustment. It shall be strong, rigid, positive and fast in operation.
8. Disagreement circuit shall be provided which shall detect pole position discrepancy.
9. The design of the circuit breaker shall be such that contacts will not close automatically upon loss of gas/ air pressure.
10. Closing release shall be capable of operating within the range of the rated voltage as specified in the data sheet. Shunt trip shall operate satisfactorily under all operating conditions of the circuit breaker up to the rated breaking capacity of the circuit breaker within the range of the rated voltages specified in the Data sheet.
11. Working parts of the mechanism shall be of corrosion resisting material. Bearings which require grease shall be equipped with pressure type grease fittings. Bearing pin, bolts, nuts and other parts shall be adequately pinned or locked to prevent loosening or changing adjustment with repeated operation of the breaker.
12. All controls, gauges, relays, valves, hard drawn copper piping and all other accessories as necessary shall be provided including the following:
13. Low pressure alarm and lock out relay with adjustable pressure setting suitable for operation on DC system.
14. A no-volt relay for remote indication of power failure for compressor motor/ Spring Charge motor.
15. As long as power is available to the motor, continuous sequence of closing and opening operations shall be possible.
16. After failure of power supply to the motor, at least one open-close-open operation of the circuit breaker shall be possible.
17. Motor rating shall be such that it requires only about 30 seconds for full charging of the closing spring.
18. Closing action of the circuit breaker shall compress the opening spring ready for tripping.
19. During closing, springs are discharged and after closing of breaker, springs shall automatically be charged for the next operation. Facility for manual charging of closing springs shall be provided. Mechanical interlocks shall be provided in the operating mechanism to prevent discharging of closing springs when the breaker is already in the closed position.
	* 1. **OPERATING MECHANISM CONTROL**
20. The breaker shall normally be operated by remote electrical control. Two electrically independent trip circuit including two trip coils per pole shall be provided. However, provision shall be made for local electrical control. For this purpose a local/remote selector switch, close and trip control switch/push button shall be provided in the breaker central control cabinet.
21. The two way Local/Remote switch shall have minimum 4 (four) pair of contacts and wiring shall be made available to monitor local/remote status from local SCADA/SAS.
22. The trip coils shall be suitable for trip circuit supervision during both open and close position of the breaker. Necessary terminals shall be provided in the central control cabinet of the circuit breaker by the CONTRACTOR.
23. The auxiliary switch of the breaker shall be positively driven by the breaker operating rod.
24. A conveniently located manual tripping lever or button shall also be provided for local tripping of the breaker and simultaneously opening the reclosing circuit. A local manual closing device which can be easily operated by one man standing on the ground shall also be provided for maintenance purpose. Direction of motion of handle shall be clearly marked.
25. Necessary platform with Ladder shall be provided for easy access to the Operating Box thereby easing out local operation/maintenance.
26. When the spring get fully charged either through motor or hand cranking, the spring charging motor and the hand cranking device should get disengaged mechanically from the charged spring and this should not be depended upon only the limit switch.
	* 1. **SF6 GAS SYSTEM**
27. SF₆ gas shall serve as an arc-quenching medium during opening/closing operation and as an insulating medium between open contacts of the circuit breaker.
28. The circuit breaker shall be single pressure type. The design and construction of the circuit breaker shall be such that there is a minimum possibility of gas leakage and entry of moisture. There should not be any condensation of SF6 gas on the internal insulating surfaces of the circuit breaker
29. All gasketted surfaces shall be smooth, straight and reinforced, if necessary, to minimise distortion and to make a tight seal, the operating rod connecting the operating mechanism to the arc chamber (SF6 media) shall have adequate seals. The SF6 gas leakage should not exceed 1% per year.
30. In the interrupter assembly there shall be an absorbing product box to minimise the effect of SF6 decomposition products and moisture. The material used in the construction of the circuit breakers shall be such as fully compatible with Sf6 gas decomposition products.
31. Each pole shall form an enclosure filled with Sf6 gas independent of two other poles (for 145 kV CBs) and the Sf6 density of each pole shall be monitored.
32. The dial type SF6 density monitor shall be adequately temperature compensated to model the pressure changes due to variations in ambient temperature within the body of circuit breaker as a whole. The density monitor shall have graduated scale and shall meet the following requirements: It shall be possible to dismantle the density monitor for checking/replacement without draining the SF6 gas by providing suitable interlocked non return valve coupling

**25.1.4 BUSHINGS AND INSULATORS**1. Bushings and Insulators shall be of Porcelain, Solid core type. 2. Bushings shall be manufactured and tested in accordance with IS: 2099 & IEC60137, while Hollow column insulators shall be manufactured and tested in accordance with IEC-62155/IS: 5621. The support insulators shall be manufactured and tested as per IS: 2544/IEC60168 and IEC-60273. The insulators shall also conform to IEC-60815 as applicable3. Porcelain used for the manufacture of bushings and insulators shall be homogeneous, free from defects, cavities and other flaws or imperfections that might affect the mechanical or dielectric quality and shall be thoroughly vitrified, tough and impervious to moisture. 4. Glazing of the porcelain shall be of uniform brown colour, free from blisters, burns and other similar defects. Bushings shall be designed to have sufficient mechanical strength and rigidity for the conditions under which they will be used. All bushings of identical ratings shall be interchangeable. 5. Puncture strength of bushings shall be greater than the dry flashover value. When operating at normal voltage, there shall be no electric discharge between the conductors and bushing which would cause corrosion or injury to conductors, insulators or supports by the formation of substances produced by chemical action. No radio interference shall be caused by the bushings when operating at the normal rated voltage. 6. Bushings shall satisfactorily withstand the insulation level specified in data sheet. **25.1.5 FIXED AND MOVING CONTACTS**  1. Main contacts shall have ample area and contact pressure for carrying the rated current and the short time rated current of the breaker without excessive temperature rise which may cause pitting or welding. Contacts shall be adjustable to allow for wear, easily replaceable and shall have minimum moving parts and adjustments to accomplish these results. Main contacts shall be the first to open and the last to close so that there will be little contact burning and wear out.  2. Arcing contacts, if provided, shall be the first to close and the last to open and shall be easily accessible for inspection and replacement. Tips of arcing and main contacts shall be silver faced.  3. If multi-break interrupters are used, they shall be so designed and augmented that a fairly uniform voltage distribution is developed across them.**25.1.6 INTERLOCKS** 1. Key release mechanical interlocks shall be incorporated in the operating mechanism for interlocking with the associated isolators, so that operation of the circuit breaker is dependent on a "key-trapped" situation. In addition, electrical interlocks with associated isolators shall be provided.**25.1.7 ADDITIONAL DUTY REQUIREMENTS** 1. Circuit breakers shall be capable of clearing short line faults with the same impedance behind the bus corresponding to the rated fault current. 2. Circuit breakers shall be capable of breaking 25% of rated fault current at twice rated voltage under out of phase conditions. 3. The Bid shall highlight the design features provided to effectively deal with: a) Breaking of inductive currents and capacitive currents. b) Charging of long lines and cables. c) Clearing developing faults within the full rating of the breaker. d) Opening on phase opposition. **25.1.8 ACCESSORIES** 1. **Gas Pressure Detector** The circuit breaker shall be provided with gas pressure monitor with temperature compensation for initiating alarm and locking the operating mechanism in the event of abnormality. **Gas pressure monitor shall be provided for each pole individually**. 2. **Position Indicator** Each pole of the circuit breaker shall be provided with a position indicator. 3. Terminals Each circuit breaker shall be provided with suitable terminal pads of high conductivity aluminium alloy for connecting to the line. 4. **Auxiliary Switches** Each circuit breaker shall be equipped with auxiliary switches with sufficient number of contacts for control, indication and interlocking purposes. Ten normally open and ten normally closed contacts shall be provided as spares. All contacts shall be rated for the DC voltage specified in data sheet. 5. **Terminal Blocks** All accessories and control devices shall be completely wired. All wirings which are connected to external circuit shall be terminated on terminal blocks installed in the control cabinet. The terminal blocks provided shall have twenty (20) percent spare terminals. 6. Operating mechanism housing shall be supplied with all required accessories including thefollowing:  a) Padlocks and duplicate keys. b) Space heaters equipped with automatic thermostatic control.  c) Local/remote changeover switch.  d) Manually operated tripping push button/lever (mechanical) conveniently located to trip all three phases simultaneously.  e) Control switches to cut off control power supplies. f) Fuses as required. g) Two earthing terminals. h) Auxiliary relays required for satisfactory operation.  i) Motor contactor with thermal release  j) Provision for mechanical interlock with isolator.  k) Readable wiring diagram shall be pasted inside the front cover of the operating mechanism box with indelible ink. **25.1.9 SUPPORT STRUCTURES**  1. The Circuit Breakers shall be suitable for mounting on steel structures.  2. The support structure shall be of steel hot dip galvanized type. The height of support structure shall be designed to keep the bottom most live part and bottom of insulators of circuit breakers at minimum clearance from the plinth as specified in data sheet.  3. All necessary galvanized bolts, nuts and washers to complete the erection shall be furnished including the embedded anchor bolts for securing the supporting structure to the concrete foundations.**25.1.10 NAME PLATES** All equipment shall have non-corrosive name plates fix at a suitable position indelibly mark with full particular there on in accordance with the standard adapted. **25.1.11 EARTHING**  Two earthing pads shall be provided on each supporting structure. Each control cabinet or terminal box mounted on the supporting structure shall also be connected to an earthing pad. Separately mounted control cabinets shall be provided with two earthing pads adjacent to the base of the cabinet. The earthing connection shall be bolted type and suitable for receiving 65mm x 12mm MS strip.**25.1.12 TERMINAL CONNECTORS** The equipment shall be supplied with required number of terminal connectors of approved type suitable for ACSR conductors. The type of terminal connector, size of connector, material, and type of installation shall be approved by the Purchaser, as per installation requirement while approving the equipment drawings. **25.1.13 TESTS**  All routine tests shall be carried out in accordance with relevant IS. All routine/acceptance tests shall be witnessed by the Purchaser/his authorized representative. The tests shall include the following:1. **Routine/Acceptance Tests (all units**)
2. Mechanical Operation tests
3. Power frequency voltage withstand test (dry)
4. Tests on auxiliary & control circuits
5. Measurement of resistance of the main circuit.

**b) Type Tests**: The bidder shall furnish type test certificates and results for the following tests along with the bid for breaker of identical design. i) Breaking and making capacity test ii) Short-time current test iii) Temperature rise tests iv) Lightning Impulse voltage test **c) Special Tests:** The operating mechanism box shall be tested for paint film thickness and the galvanization test for structure shall be conducted in one of the unit of each type. **d) Test Certificates** Copies of routine/acceptance test certificates shall be produced with the endorsement of the inspecting authority to the Purchaser before effecting dispatch. The test report shall contain the following information.i) Complete identification data, including serial No. of the breaker. ii) Method of application, where applied, duration and interpretation of results in each test.**25.1.14 PRE-COMMISSIOING TESTS** (a) Contractor shall carry out following tests as pre-commissioning tests. Contractor shall also perform any additional test based on specialties of the items as per the field instructions of the equipment Supplier or Employer without any extra cost to the Employer. The Contractor shall arrange all instruments required for conducting these tests along with calibration certificates and shall furnish the list of instruments to the Employer for approval:(a)Insulation resistance of each pole. (b)Check adjustments, if any suggested by manufacturer. (c)Breaker closing and opening time. (d)Slow and Power closing operation and opening. (e)Trip free and anti-pumping operation. (f) Minimum pick-up voltage of coils. (g)Dynamic Contact resistance measurement. (h)Functional checking of control circuits interlocks, tripping through protective relays andauto reclose operation.(i) Insulation resistance of control circuits, motor etc. (j) Resistance of closing and tripping coils. (k)SF6 gas leakage check. (l) Dew Point Measurement (m) Verification of pressure switches and gas density monitor. (n)Checking of mechanical ‘CLOSE’ interlock, wherever applicable. (o)Testing of grading capacitor. (p)Resistance measurement of main circuit. (q)Checking of operating mechanism. (r) Check for annunciations in control room**25.1.15 SPECIAL TOOLS AND TACKLES** The Bidder shall furnish a list of any special tools and tackles required for maintenance and operation purposes with recommended quantities **25.1.16 Guaranteed Technical Particulars (GTP):**

|  |  |  |  |
| --- | --- | --- | --- |
|  | Particulars  | Unit | Data for 132 kV CB |
| 1 | Type  |  | SF6 |
| 2 | No. of Poles  |  | 3 (3 Phase Ganged Unit) |
| 3 | Service |  | Outdoor |
| 4 | Rated System Voltage | kV | 132 |
| 5 | Highest System Voltage | kV(RMS) | 145 |
| 6 | System earthing |  | Solidly earthed system |
| 7 | Rated Voltage of Breaker | kV | 145 |
| 8 | Rated Continuous Current | Amps | Upto 3150 A |
| 9 | Rated Frequency | Hz | 50 |
| 10 | Rated Short Circuit breaking current (I) – 3 sec - symmetrical | kA | 40 |
| 11 | Rated Short Circuit making current | kAp | 108 |
| 12 | Duty cycle |  | 0-0.3 Sec-CO-3Min –CO |
| 13 | First pole to clear factor |  | 1.3 |
| 14 | Operating time |  |  |
| i) Opening Time | ms | Not exceeding 50ms |
| ii) Closing Time | ms | Not exceeding 120ms |
| 15 | Insulation level |  |  |
| i) Power Frequency with Stand Voltage | kV(RMS) | 275 |
| ii) Impulse withstand Voltage | kVp | 650 |
| 16 | Minimum clearance between live part (upper phase) | mm | 1380 (Min. clearance between phases (centre to centre) – 1700mm |
| 17 | Minimum clearance between live part to earth | mm | 1260 |
| 18 | Minimum Ground clearance (from bottommost live part to plinth level) | mm | 4600 |
| 19 | Minimum clearance from bottom Of Support insulator to plinth level | mm | 3200 |
| 20 | i) Minimum Creepage Distance (Total) | mm | 4495 |
| ii) Minimum Creepage Distance (Protected) | mm |  |
| 21 | Arcing horn |  |  |
| 22 | Operating mechanism: |  | Motorized  |
|  | a) Type |  | Spring Charged mechanism |
|  | b) Rating of Drive Motor | V | Universal Motor/ 1 Phase 50 Hz 230V AC |
|  | c) Rated voltage of Shunt trip coil & operating range | V. DC |  110V [50% - 110%] |
|  | (d) Rated voltage of Closing coil & operating range | V. DC |  110V [80% - 110%] |
|  | (e) No. of trip coils | No | 2 per CB |
|  | (f) No. of closing coils | No | 1 per CB |
|  | g) No of spare auxiliary contacts & contact rating | Nos. AMPS | 10 N/O+10 N/C (per CB) 10A at 240V AC & 2A at 220V/110V DC |
|  | h) Minimum thickness of sheet steel forcontrol cabinet | mm | 3 |
|  | i) Enclosure Protection |  | IP55 |
| 23 |  Reclosing |  | Three Phase Auto Reclosing |
| 24 | Support structure (Painted / Galvanised) |  | Galvanised |
| 26 | All other parts (Painted / Galvanised) |  | Synthetic enamel shade 631 of IS5(125 microns) |
| 27 | Minimum size of control wiring (Copper) | Sqmm | 2.5 |

 |
| 2hal | * 1. **TESTS**

All the tests specified below shall be carried out in accordance with the Indian Standards by the manufacturer in the presence of Purchaser’s representative. If the cable fails to pass the test specified, the Purchaser shall have the option to reject it. Shipping release shall be obtained from the Purchaser's representative. The Purchaser, however reserves the right to waive off the inspection.The tests at works shall include electrical, mechanical, and hydraulic tests in accordance with the appropriate clauses of Statutory Regulation, relevant codes, and standards, in addition any test called for by the Purchaser or his representative to ensure that the equipment being supplied fulfils the requirement of the specification.For test not covered by any code or specifically mentioned in this specification, the test procedures are to be agreed with the Purchaser.1. **GUARANTEE**

All the cables shall be guaranteed against faulty material, defective design & poor workmanship for a period of 18 months from the date of commissioning. The materials becoming defective during the guarantee period shall be replaced free of cost and the defects arising out of the works shall be rectified free of charge without delay.**29. QUALITY ASSURANCE** To ensure that the supply under the scope of this Contract whether manufactured or performed within the Contractor's works or at his Sub Contractor's premises or at site or at any other place of work are in, accordance with the specifications, the Contractor shall adopt suitable quality assurance programme to control such activities at all points necessaryThe Quality plan shall be mutually discussed and approved by the Employer. The Contractor shall be required to submit all the Quality Assurance Documents as stipulated in the Quality Plan at the time of Employers inspection of equipment/material. 2.8.2 The Employer or his duly authorized representatives reserves the right to carry out Quality Audit and quality surveillance of the systems and procedures of the Contractors/his vendors Quality Management and Control Activities. |
| **30.0** | **Contract Agreement:** |
| 30.1 |  An agreement shall have to be drawn on non-judicial stamp of appropriate value with the Department by the selected Contractor in AEGCL’s General Conditions of Supply and Erection 2009 of contract within 15 (fifteen) days from the date of issue of the LOI/Work Order.  |
| 30.2 | Wherever there is any variation in between the conditions of the AEGCL’s General Conditions of Supply and Erection 2009 and the above terms & conditions, this bid conditions will supersede the conditions of the AEGCL’s General Conditions of Supply and Erection 2009.  |
| **31.0** | **Liquidated Damage:** |
|  | The date of completion of work shall be deemed to be the essence of the contract and shall not be completed no later than the date specified in the contract. In case of failure to complete the work within the stipulated period AEGCL shall be entitled to:  |
| 31.1 | Recover an amount at the rate of 1% (One percent) of the Contract Price per week or part thereof of delay, subject to maximum of 10% (Ten percent) of the contract price as liquidated damage to AEGCL.However, the payment of liquidated damages shall not in any way relieve the Contractor from any of its obligations to complete the works or from any other obligations and liabilities of the Contractor under the Contract.  |
| 31.2 | To complete the balance work giving notice to the Contractor/Firm and to recover any extra expenditure incurred thereby for having to complete the work at a higher price at the risk and responsibility of the Contractor/Firm. |
| 31.3 | Contractual failure: - Refer clause No.27.1 of AEGCL’s General Conditions of supply and erection 2009. |
| **32.0** | **PERT Chart and/or BAR Chart:**  |
|  | The successful bidder within 10 (ten) days before the contract is awarded will make out a detailed PERT Chart covering all activities along with detailed program chart on accepted scheme indicating various stages of execution, method of execution and completion of work in different stages keeping the period of completion in view and submit the same to the Engineer for the consideration and approval. |
| **33.0** | **Insurance:**  |
|  | The bidder shall arrange for any pay/cost of personnel accident insurance, medical treatment etc. in respect of their employees assigned to the works for all time and shall govern by Law of land. |
| **34.0** | **Warranty:** |
| 34.1 | The Supplier/Manufacturer warrants that all the Goods are new, unused, and of the most recent or current models, and that they incorporate all recent improvements in design and materials, unless provided otherwise in the Contract. |
| 34.2 | The Supplier/Manufacturer further warrants that the Goods shall be free from defects arising from any act or omission of the Supplier or arising from design, materials, and workmanship, under normal use in the conditions prevailing in the country of destination. The supplier will provide warranty for the works executed by them.  |
| 34.3 | If during the Period Warranty any defect is found, the Purchaser shall give Notice to the Supplier/Manufacture stating the nature of any such defects together with all available evidence thereof, promptly following the discovery thereof. The Purchaser shall afford all reasonable opportunity for the Supplier/Manufacturer to inspect such defects. |
| 34.4 | If having been notified, the Supplier/Manufacturer fails to remedy the defect within a period of 15 (fifteen) days, the Purchaser may, following notice to the Supplier/Manufacturer, proceed to do such work, and the reasonable costs incurred by the Purchaser in connection therewith shall be paid to the Purchaser by the Supplier or may be deducted by the Purchaser from any amount due the Supplier or claimed under the Performance Security.  |
| 34.5 | The term period of warranty shall mean the period of 18 months from the date of Taking Over of the Work by AEGCL. A Taking over Certificate (TOC) will be issued by the appropriate authority. The successful bidder should warrant the free replacement of any damaged/malfunctioning switchgear or measuring equipment and its accessories during the warranty period. |
| **35.0** | **Safety:** |
| 35.1 | Each and every safety measures for MAN and MACHINE will be the sole responsibility of the Contractor without any prejudice. Compensation claim if any will also be the responsibility of the contractor without any prejudice. As the contract is Turnkey in nature hence AEGCL will not bear any responsibility towards such claim. |
| **36.0** | **Pollution:** |
|  | Each and every measure should be taken to adhere to the standard norms to avert any occasion of Air Pollution, Water Pollution, Soil Pollution and Sound Pollution. In case of any deviation leading to any legal action the Contractor will be solely responsible without any prejudice. |
| **37.0** | **Payment terms:** |
| 37.1 | No advance/Mobilization advance shall be made in this contract.  |
| 37.3 | Payment will be made by DGM, (T&T) Circle, AEGCL, Garmur,Jorhat. The Bidder / Firm will have to be submitted the following Net Banking details. (a) Banker’s Name & Branch (b) Account No (c) Banker’s address (d) Banker’s IFSC Code (e) Banker’s RTGS Code  |
| **38** | **Performance security deposit:** |
| 38.1 | The successful bidder shall have to deposit through a **Bank Guarantee** from a Nationalized or scheduled Bank of RBI in AEGCL’s standard proforma on non-judicial stamp of appropriate value for an amount equivalent to 10% (ten percent) of the total value of the order as performance security, immediately within 10 (ten) days from the issue of the letter of intent/detailed orders (as the case may be), duly pledged in favour of **MD**, **AEGCL, Bijulee Bhawan, Paltanbazar, Guwahati-1,** and such security deposit shall be valid up to 30 days beyond the warranty period of 18 (Eighteen) months. The Bank Guarantee (BG) should be submitted to the **O/O the Deputy General Manager, T&T Circle, AEGCL, Garmur,Jorhat-785007** by the issuing Bank under registered post AD.  |
| 38.2 | Please note that, if the selected Bidder / Firm fails to furnish the requisite performance security as stated above and signs the contract within the stipulated period, 10 percent security money will be deducted from the total Bill value. |
| 38.3 | If the bidder / firm fails or neglects to observe and perform any of his obligations under the contract, Purchaser (AEGCL) shall have the right to forfeit either in full or in part at his absolute discretion, the security deposit furnished by the Contractor/Firm. |
| 38.4 | No interest shall be payable on such deposits. |
| **39.0** | **Force Majeure Condition:**  |
|  | Force Majeure condition shall be considered as any circumstances beyond reasonable control of the party claiming relief, including but not limited to strikes, lockout, civil commotion, riot insurrection, hostilities, mobilization, war, fire, flood, earthquake, malicious damage, or accidents could entitle contractor to extension time. Any such delay should be intimated within 10 (ten) days from the beginning of such delay to consider/approved, any claim without prior information may not be considered under force Majeure. |
| **40.0** | **Settlement of Dispute and Arbitration:**  |
|  | Any dispute arising out of the contract will be first settled bilaterally between AEGCL and Contractor. In case, dispute cannot be settled bilaterally, it will be referred to arbitration to be by an arbitrator appointed by AEGCL. The contractor shall not stop the work during settlement of any dispute. All disputes shall be subjected to the jurisdiction of District Court of Kamrup District. |
| **41.0** | **Right to Reject:**  |
|  | AEGCL reserves the right to reject any or all the bids without assigning any reason thereof and the AEGCL further reserves the right to split up the work order in favour of more than one Contractor. The AEGCL also reserves the right to reject the lowest or any other price without assigning any reason. |
|  **The clauses which are not appearing in this document (bid) will be as per The General Condition of Supply and Erection 2009 of AEGCL. The General Condition of Supply and Erection 2009 of AEGCL is available in the AEGCL’s website www.aegcl.co.in under Acts, Rules, and Policies Tab.** |
|  |

**Letter of Technical Bid**

[Bidder’s Letterhead]

Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Tender No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Invitation for Bid No.:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

To:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

We, the undersigned, declare that:

1. We have examined and have no reservations to the Bidding Document, including Addenda No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_.
2. We offer to supply in conformity with the Bidding Document and in accordance with the completion/delivery schedule specified in the bid document, the following Goods and Related Services: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_
3. Our Bid shall be valid for a period of \_\_\_\_\_\_\_\_ days from the date fixed for the bid submission deadline in accordance with the Bidding Document, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;
4. If our Bid is accepted, we commit to obtain a Performance Security in the amount of \_\_\_\_\_\_\_ percent of the Contract Price for the due performance of the Contract;
5. We are not participating, as Bidders, in more than one Bid in this bidding process;
6. We understand that this Bid, together with your written acceptance thereof included in your notification of award, shall constitute a binding contract between us, until a formal Contract is prepared and executed.
7. Our firm, its affiliates, or subsidiaries, including any Subcontractors or Suppliers for any part of the contract, has not been declared ineligible by AEGCL, APDCL or APGCL under the Employer’s country laws or official regulations
8. We understand that you are not bound to accept the lowest evaluated bid or any other bid that you may receive.

Name \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

In the capacity of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Signed \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Duly authorized to sign the Bid for and on behalf of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Price Proposal Submission Sheet**

Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Tender No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Invitation for Bid No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

To: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

We, the undersigned, declare that:

1. We have examined and have no reservations to the Bidding Document, including Addenda No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_
2. We offer to supply in conformity with the Bidding Document and in accordance with the completion/delivery schedule specified Schedule of Supply & Erection, the following Goods and Related Services: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_
3. The total price of our Bid, excluding any discounts offered in item (d) below is: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_
4. The discounts offered and the methodology for their application are: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_
5. The following commissions, gratuities, or fees have been paid or are to be paid with respect to the bidding process or execution of the Contract:

|  |  |  |  |
| --- | --- | --- | --- |
| Name of Recipient | Address | Reason | Amount |
|  |  |  |  |
|  |  |  |  |

(If none has been paid or is to be paid, indicate “none.”)

Name \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

In the capacity of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Signed \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Duly authorized to sign the Bid for and on behalf of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Date \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Bidding Forms:**

**Name of work:**

**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**Bid Identification No:**

 **\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**General**

1. Name of the Firm/Contractor:
2. Full Address:
3. Constitution of the Firm:

a) Whether Partnership or any type:

**A) Experience**

1. No of years the Firm/Contractor has been in operation under its present name.
2. Details of work executed/being executed by the tenderer in the last three years.
3. Testimonials from Clients Company on various works executed for the last three years.

 (Details of works executed/under execution in the last three years including other department)

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Sl.****No.** | **Name of work & W/O No.** | **Worked Done Under** | **Value of Work** | **Specified date of completion** | **Present status/completed on** |
|  |  |  |  |  |  |

**B) Financial Position**

(i) Financial Turnover during the last three years (copies of Audited Annual report, Accounts or a statement duly certified by a chartered accountant and Income Tax return.

|  |  |
| --- | --- |
| **Year** | **Turn over** |
|  |  |

Any other details that the tenderer may like to furnish to substantiate their financial and technical ability to undertake this work and complete the same within stipulated period of completion.

Name of the Bidder: -

 Signature of the Bidder/Firm …………………………………….

 Full Name ……………………………………………………………....

 Postal Address ………………………………………………………...

Phone/Mobile No. …………………………………………………

**PRICE BID**

**PRICE SCHEDULE**

***(To be submitted in the Part-II, ‘Price bid’ in sealed envelope in quadruplicate)***

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. No | Item Description | Qty | Unit | Rate(in Rs) | Amount (in Rs) |
| 1. | Supply of 145kV,3150A,31.5KA for 3 sec Gang operated SF6 breaker | 2 | Set |  |  |
| 2 | F&I | 2 | Set |  |  |
| Total inclusive of F&I  |  |
| Add 18% GST |  |
| **Grand Total** |  |

 Name of the Bidder: -

 Signature of the Bidder/Firm …………………………………….

 Full Name …………………………………………………………………

Postal Address ………………………………………………….………

 Phone/Mobile No. …………………………………………….…….

 **Form of Bid Security (Bank Guarantee)**

(To be stamped in accordance with Stamp Act)

(The non-Judicial Stamp Paper should be in the name of issuing Bank)

Date: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Bid Reference No.: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

WHEREAS, \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Name of Bidder]* (hereinafter called "the Bidder") has submitted his bid dated \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Date]* for the supply of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Name of Contract]* (hereinafter called "the Bid").

KNOW ALL MEN by these presents that We \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Name of Bank]* of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Name of Place]* having our registered office at \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ (hereinafter called "the Bank) are bound unto \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ *[Name of Purchaser]* (hereinafter called "the *Purchaser* ") in the sum of \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_1 for which payment well and truly to be made to the said Purchaser the Bank binds himself, his successors and assigns by these presents.

SEALED with the Common Seal of the said Bank this \_\_\_ day of\_\_\_\_\_\_\_ 20\_\_\_.

**THE CONDITIONS of this obligation are:**

1. If the Bidder withdraws its Bid during the period of bid validity specified by the Bidder in the Bid Submission Sheet, except as provided in the relevant Bid ***Clause***;

Or

1. If the Bidder refuses to accept the correction of errors in his Bid;

Or

1. if the Bidder, having been notified of the acceptance of his Bid by the Employer during the period of Bid validity;
2. fails or refuses to execute the Form of Contract Agreement in accordance with the Instructions to Bidders, if required; or
3. fails or refuses to furnish the Performance Security, in accordance with the Instructions to Bidders;

We undertake to pay to the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it owing to the occurrence of one or all the three conditions, specifying the occurred condition or conditions.

This Guarantee will remain in force up to and including the date \_\_\_\_days after the deadline for submission of bids as such deadline is stated in the Instructions to Bidders or as it may be extended by the Purchaser, notice of which extension(s) to the Bank is hereby waived. Any demand in respect of this Guarantee should reach the Bank not later than the above date.

DATE \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ SIGNATURE OF THE BANK \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

WITNESS \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ SEAL \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(Signature, Name, and Address

**ANNEXURE: I**

***Following information is to be furnished in the ‘Technical and Commercial bid’ as first page***.

(Please tick mark where necessary.)

|  |  |  |
| --- | --- | --- |
| 1) | Earnest money (EMD) | : Submitted/Not submitted |
|  | a) Amount of EMD | : Rs. |
|  | b) Submitted in the form of |  |
|  | Bank Guarantee /Demand Draft | : Yes/No. |
| 2) | Validity of the offer | : ……. days from the date of opening of ‘Technical & Commercial Bid’ & ‘Price bid’. |
| 3) | Nature of price offered |  |
|  | 1. ‘FIRM’ Price
 | : Yes/No |
| 4) | Terms of payment(Whether agreeable to accept payment as specified in clause- 37) | : Yes/No |
| 5) | Date of completion of supply/Erection.(Please specify the date of completion of supply/Erection as per specification) | : Yes/No |
| 6) | ‘Security and performance guarantee’(Whether agreeable to accept as specified in Clause no-34&35) | : Yes/No |
| 7) | List of orders executed for similar works furnished | : Yes/No |
| 8) | Performance certificate from the Govt/Govt undertaking furnished | : Yes/No |
| 9) | Deviation from the specifications |  |
| 1. Technical
 | : Yes/No |
| 1. Commercial
 | : Yes/No |
| 10) | Information in respect of technical capability is furnished | : Yes/No |
| 11) | Information in respect of financial capability certificate from the Banker is furnished as per Cl. No. 15.3.6 and 15.3.7 | : Yes/No |
| 12) | PAN card as per Cl. No. 15.3.2 | : Yes/No |
| 13) | GST registration no. as per Cl. No. 15.3.4  | : Yes/No |
| 14) | Registered Power of Attorney as per Cl.no. 15.3.5enclosed. | : Yes/No |

 Name of the Bidder: -

 Signature of the Bidder/Firm …………………………………….

 Full Name ……………………………………………………………

 Postal Address ………………………………………………………

 Phone/Mobile No. …………………………………………………

**ANNEXURE-II**

### **GUARANTEED TECHNIICAL AND OTHER PARTIICULARS**

***(To be filled in by Bidder and shall be furnished with the Technical Bid)***

***1. 132kV Circuit Breaker***

| **Sl No.** | **Particulars** | **Unit** | **Data for 132kV CB** |
| --- | --- | --- | --- |
| **I** | **II** | **III** | **IV** |
|  | Type |  |  |
|  | No of Poles |  | (3 phase Ganged Unit) |
|  | Service |  |  |
|  | Rated System Voltage | kV |  |
|  | Highest System Voltage | kV |  |
|  | System earthing |  |  |
|  | Rated Voltage of Breaker | kV |  |
|  | Rated Continuous Current | Amps |  |
|  | Rated Frequency | Hz |  |
|  | Rated Short Circuit breaking current(I-3secs-symmetrical) | kA RMS |  |
|  | Rated Short Circuit making current | kA PEAK |  |
|  | Duty cycle |  |  |
|  | First pole to clear factor |  |  |
|  | Operating time |  |  |
| i) Opening Time | ms |  |
| ii) Closing Time | ms |  |
|  | Insulation level |  |  |
|  | i) One minute Power Frequency withstand Voltage (Dry) | kV RMS |  |
|  | ii) Full Wave Impulse withstand Voltage (1.2/50µsec) | kV Peak |  |
|  | Minimum clearance between phase | mm |  |
|  | Minimum clearance between phase to earth. | mm |  |
|  | Minimum Ground clearance (from bottom most live part to plinth level) | mm |  |
|  | Minimum clearance from bottom of support insulator to plinth level. | mm |  |
|  | Minimum Creepage Distance |  |  |
|  | i) Total | mm |  |
|  | ii) Protected | mm |  |
|  | Operating mechanism |  |  |
|  | a) Type |  |  |
|  | b)Rated 3 Phase, 50Hz Voltage for Drive Motor. | V |  |
|  | c) Rated voltage of Shunt trip coil & operating range. | V.DC |  |
|  | d) Rated voltage of Closing coil & operating range. | V.DC |  |
|  | e) No. of trip coils | No |  |
|  | f) No. of closing coils | No |  |
|  | g) No of spare auxiliary contacts & contact rating. | Nos. AMPS |  |
|  | h) Minimum thickness of steel sheet for control cabinet. |  |  |
|  | i) Enclosure Protection. |  |  |
|  | Reclosing |  |  |
|  | Support Structure (painted/Galvanised) |  |  |
|  | All other parts (painted/Galvanised) |  |  |
|  | Minimum size of control wiring (Copper) | Sq. mm |  |

|  |
| --- |
|  |