BUSBAR DIFFERENTIAL PROTECTION

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Is busbar differential protection present in the substation at: - 400kV Bus: - 220kV Bus: - 132kV Bus: |  |  |
| 2 | Is the scheme of Busbar differential protection Centralized or Decentralized? In case of decentralized busbar scheme, Are all the peripheral units healthy? Is the connectivity of the peripheral units to the Main Central Unit healthy? |  |  |
| 3 | Are both Check Zone and bus Zone features present? |  |  |
| 4 | Are the Status of Bus Isolators, Circuit Breakers, Line Isolators (if taken) properly reporting to the busbar relay? |  |  |
| 5 | Note down the present values from the busbar differential relay: Bus Zone A Current: Differential: Restraint: Bus Zone B Current: Differential: Restraint: |  |  |
| 6 | Is DT send logic configured in the busbar relay for transmission lines? |  |  |
| 7 | Is LBB an inbuilt feature of the busbar protection? |  |  |
| 8 | Are the feeders properly segregated among the buses (trend analysis of load and demand) so that in case of tripping of one bus bar, the other bus or feeders connected to the healthy bus is not overloaded? |  |  |