Disturbance Recorder

| Sl No. | PARTICUARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Are the settings of Disturbance Recorder maintained as below: Pre-fault time: 0.5s Post-fault time: 2.5s Recording Window: 3s DR triggering Criteria: Any Start or Trip of a Protection Event |  |  |
| 2 | The DR Channels are standardized comprising of all Analog Inputs, Digital Inputs, Protection Start and Trip signals. The DR is time synchronized (As per clause No. 17 of IEGC 2023) |  |  |
| 3 | On case of any trip/fault event, the DR data is sent to Protection team within 24 hours for analysis and facilitating report uploading in the NERLDC Portal (As per Clause No. 37.2 of IEGC 2023) |  |  |