33kV OUTGOING

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Non-Directional Overcurrent and Earth fault protection functions is enabled (IDTM Normal Inverse Curve) |  |  |
| 2 | Availability of Under/Over frequency, df/dt Under/Over voltage protection functions is available in the 33kV relays. (The protections are to be turned on only if there is a special case of system requirement as per studies) |  |  |
| 3 | What is the basis of Overcurrent setting? (CT Ratio or Loading of the line) |  |  |
| 4 | Is the Earthfault pickup set at 80A? (In case of lightly loaded line, is the earth fault pickup is kept keeping in view the zero-sequence current during single phase open circuit fault?) |  |  |
| 5 | Inrush/Harmonic restrained feature is enabled? |  |  |
| 6 | Highset pickup of OC and EF is kept in between 3A to 5A with a time delay of 50ms? If any other setting is kept (verify) |  |  |
| 7 | Any instance of 33kV Feeder tripping overreach a fault in the downstream distribution feeders? |  |  |
| 8 | Is the TMS for Overcurrent and Earthfault is fixed at 0.1? (Please verify if other values of TMS is set) Note: The DISCOM substations should set their TMS w.r.t grid substations |  |  |