TRANSMISSION LINES

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Main-1 and Main-2 protection relays available at 400kV/220kV level of “different make” or “same make with difference operating characteristics”? Main and Backup protection relays available at 132kV level? |  |  |
| 2 | Is Auto-Reclosure protection switched ON for transmission lines (SPAR at 400kV/220kV and TPAR at 132kV level) SPAR: Single Pole Auto-Reclosure TPAR: Three Pole Auto-Reclosure |  |  |
| 3 | Distance Protection Settings: Setting Parameters are calculated with Standard Conductor Parameters? Zone 1: 80% of the line at 0s Zone 2: 120% of the line (Single Ckt) 150% of the line (Double Ckt) Is chances Zone 2 overreaching into the next adjacent short line at remote bus considered and Time delay set accordingly (350ms or 500ms) Zone 3: 1.2 times of (Protection Line + longest line at Remote Bus), Delay: 800ms and 1s at 400kV Zone 4: 20% of the Protected line, Line<100km 10% of the Protected line, Line>100km Zone 4 Delay: 500ms |  |  |
| 4 | Are the resistive reaches calculated keeping in view the Tower footing resistance, arc resistance, remote end infeed effect? |  |  |
| 5 | What are the reaches and time delays kept for traction lines: Zone 1: Zone 2: Zone 3: Zone 4: Is AR kept enabled for traction lines? |  |  |
| 6 | Is mutual compensation wiring and settings present for double circuit lines? |  |  |
| 7 | Is power swing block enabled? Logic: All zones blocked. Unblock time kept at 2 seconds. Zone 2 and higher zones blocked Is out of step trip enabled? |  |  |
| 8 | Is switch onto fault enabled? SOTF initiation is based on “Manual Close Input to the relay-Hardware logic” Auto-initiation using “current & voltage” is enabled? What is the SOTF reach? |  |  |
| 9 | VT fuse fail is used for alarm? Broken conductor is used for alarm? |  |  |
| 10 | “Load Encroachment” if enabled has been done studying the requirement in lines prone to heavy loading (e.g. heavily loaded double circuit lines in case of loss of one circuit)? |  |  |
| 11 | Over/Undervoltage is enabled/disabled? Settings (if enabled) Over/Underfrequency is enabled/disabled? Settings (if enabled) Voltage and frequency-based protection are enabled only when the requirement is considered necessary after detailed study (or instructed and approved by SLDC/NERLDC/NERPC) |  |  |
| 12 | For Lines with scheme (Main 1 and Main 2 protection relay), Dir. OC is disabled and DEF is enabled? |  |  |
| 13 | Are the Dir. EF settings kept considering the ROT of Zone 3 Protection and studying the trend of 3Io current/fault analysis/Bus fault studies? Highset is kept disabled? |  |  |
| 14 | For 132kV Lines, OC and EF are to be kept disabled in the distance relay and enabled in the backup protection relay. The ROT of Dir. OC should be more than the Zone 2 operating time and ROT of DEF should be more than the Zone 3 operating time Highset is kept disabled? |  |  |
| 15 | Carried Aided Protection is present for the line? POTT or PUTT For short double circuit lines, Current reversal logic is enabled? |  |  |