SUBSTATAION AUXILIARIES

DC SYSTEM

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Are two different DC sources (Battery Banks/Chargers) (110V/220V) available at the substation? |  |  |
| 2 | DC Source 1 Parameters: Measure Voltage: +VE to Earth: -VE to Earth: Presence of DC earth fault in Source 1? Age of Battery Bank 1: Date of last discharge test: Measurement of voltages with: Charger ON: Charger OFF: Measurement of individual cell voltage healthy? DC Source 2 Parameters: Measured Voltage +VE to Earth: -VE to Earth: Presence of DC earth fault in Source 2? Age of Battery Bank 2: Date of last discharge test: Measurement of voltages with: Charger ON: Charger OFF: Measurement of individual cell voltage healthy? |  |  |
| 3 | Are two different 48V DC sources available at the substation? |  |  |
| 4 | 48V Source 1 Measured Voltage: Age of Battery Bank 1: Date of last discharge test: Measurement of individual cell voltage healthy? 48V Source 2 Measured Voltage: Age of Battery Bank 2: Date of last discharge test: Measurement of individual cell voltage healthy? |  |  |
| 5 | Is AC supply available in the Battery room/Charger room? |  |  |

AC SOURCES

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | List of Station Transformers: Station Transformer#1 Details: Date of Commissioning: Station Transformer#2 Details: Date of Commissioning: |  |  |
| 2 | List of Diesel Generators: Diesel Generator#1 Details: Date of Commissioning: Diesel Generator#2 Details: Date of Commissioning: |  |  |
| 3 | Automatic/Manual changeover present in the sub sub-station between Station AC supply and Diesel Generator Supply? Is periodic maintenance work carried out for the Generator? (Run the Generator/Manual Start/Visual Inspection/filters/lubrication/cleaning/cooling system service/batteries/check intake-exhaust etc.?) Status Diesel Generator#1: Status Diesel Generator#2: |  |  |
| 4 | Check AC supply at Substation Level: Voltage Measurement: Phase to Neutral: Phase to Earth: Neutral to Earth: Is the earthing healthy for control room AC supply? |  |  |
| 5 | Power Supply to SAS PCs/DRPCs/Metering PCs are available for both AC sources and backup battery banks through inverters? Any case of Computer Workstation failure/sudden power cut to PCs/damaged SMPS recorded in the control room? |  |  |