INTERNAL PROTECTION AUDIT

ASSAM ELECTRICITY GRID CORPORATION LIMITED

(In compliance with Clause 15 of Indian Electricity Grid Code, 2023)

| Name of Substation: |  |
| --- | --- |
| Date of Protection Audit: |  |
| Name of Auditors: |  |

TABLE OF CONTENTS

- SUBSTATION AUXILLIARIES						PAGE Nos.

- DC SOURCES …………………………………………………………………………………………………..3

- AC SOURCES ……………………………………………………………………………………………………4

- TRANSMISSION LINES ……………………………………………………………………………………………5

- POWER TRANSFORMERS ………………….……………………………………………………………………7

- REACTORS ……………………………………………………………………………………………….…………….9

- BUSBAR DIFFERENTIAL PROTECTIO ……………………………………………………………………….10

- 33kV OUTGOING FEEDER………………..……………………………………………………………………..11

- DISTURBANCE RECORDERS …………………………………………………………………………………….12

- DISCOM END PROTECTION CHECKLIST ……………………………………………………………………13

- ANNEXURES:

- SINGLE LINE DIAGRAM ………………………………………………………………………………14.

- TRANSMISSION LINE DETAILS ……………………………………………………………………..15

- TRANSFORMER DETAILS ……………………………………………………………………………..16

- 33kV OUTGOING FEEDER DETAILS ……………………………………………………………….17

- SUBSTATION AUXILIARIES

- DC SOURCES

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Are two different DC sources (Battery Banks/Chargers) (110V/220V) available at the substation? |  |  |
| 2 | DC Source 1 Parameters: Measure Voltage +VE to Earth: -VE to Earth: Presence of DC earth fault in Source 1? Age of Battery Bank 1: Date of last discharge test: Measurement of voltages with: Charger ON: Charger OFF: Measurement of individual cell voltage healthy? DC Source 2 Parameters: Measured Voltage +VE to Earth: -VE to Earth: Presence of DC earth fault in Source 2? Age of Battery Bank 2: Date of last discharge test: Measurement of voltages with: Charger ON: Charger OFF: Measurement of individual cell voltage healthy? |  |  |
| 3 | Are two different 48V DC sources available at the substation? |  |  |
| 4 | 48V Source 1 Measured Voltage: Age of Battery Bank 1: Date of last discharge test: Measurement of individual cell voltage healthy? 48V Source 2 Measured Voltage: Age of Battery Bank 2: Date of last discharge test: Measurement of individual cell voltage healthy? |  |  |
| 5 | Is Air-Condition available in the Battery room/Charger room? |  |  |

- AC SOURCES

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | List of Station Transformers: Station Transformer#1 Details: Date of Commissioning: Station Transformer#2 Details: Date of Commissioning: |  |  |
| 2 | List of Diesel Generators: Diesel Generator#1 Details: Date of Commissioning: Diesel Generator#2 Details: Date of Commissioning: |  |  |
| 3 | Automatic/Manual changeover is present in the sub-station between Station AC supply and Diesel Generator Supply? Is periodic maintenance work carried out for the Generator? (Run the Generator/Manual Start/Visual Inspection/filters/lubrication/cleaning/cooling system service/batteries/check intake-exhaust etc.?) Status Diesel Generator#1: Status Diesel Generator#2: |  |  |
| 4 | Check AC supply at Substation Level: Voltage Measurement Phase to Neutral: Phase to Earth: Neutral to Earth: Is the earthing healthy for control room supply? |  |  |
| 5 | Power Supply to SAS PCs/DRPCs/Metering PCs are available for both AC sources and backup battery banks through inverters? Any case of Computer Workstation failure/sudden power cut to PCs/damaged SMPS recorded in the control room? |  |  |

- TRANSMISSION LINE PROTECTION

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Main-1 and Main-2 protection relays available at 400kV/220kV level of “different make” or “same make with difference operating characteristics”? Main and Backup protection relays available at 132kV level? |  |  |
| 2 | Is Auto-Reclosure protection switched ON for transmission lines (SPAR at 400kV/220kV and TPAR at 132kV level) SPAR: Single Pole Auto-Reclosure TPAR: Three Pole Auto-Reclosure |  |  |
| 3 | Distance Protection Settings: Setting Parameters are calculated with Standard Conductor Parameters? Zone 1: 80% of the line at 0s Zone 2: 120% of the line (Single Ckt) 150% of the line (Double Ckt) Is chances of Zone 2 overreaching into the next adjacent short line at remote bus considered and Time delay set accordingly (350ms or 500ms) Zone 3: 1.2 times of (Protection Line + longest line at Remote Bus), Delay: 800ms, 1s at 400kV Zone 4: 20% of the Protected line, Line<100km 10% of the Protected line, Line>100km Zone 4 Delay: 500ms |  |  |
| 4 | Are the resistive reaches calculated keeping in view the Tower footing resistance, arc resistance, remote end infeed effect? |  |  |
| 5 | What are the reaches and time delays kept for traction lines: Zone 1: Zone 2: Zone 3: Zone 4: Is AR kept enabled for traction lines? |  |  |
| 6 | Is mutual compensation wiring and settings present for double circuit lines? |  |  |
| 7 | Is power swing block enabled? Logic: All zones blocked. Unblock timer kept at 2 seconds. Zone 2 and higher zones blocked Is out of step trip enabled? |  |  |
| 8 | Is switch onto fault enabled? SOTF initiation is based on “Manual Close Input to the relay-Hardware logic” Is Auto-initiation using “current & voltage” is enabled? What is the SOTF reach? |  |  |
| 9 | VT fuse fail is used for alarm? Broken conductor is used for alarm? |  |  |
| 10 | “Load Encroachment” if enabled has been done studying the requirement in lines prone to heavy loading (e.g. heavily loaded double circuit lines in case of loss of one circuit)? |  |  |
| 11 | Over/Undervoltage is enabled/disabled? Settings (if enabled) Over/Underfrequency is enabled/disabled? Settings (if enabled) |  |  |
| 12 | For Lines with scheme (Main 1 and Main 2 protection relay), Dir. OC is disabled and DEF is enabled? |  |  |
| 13 | Are the Dir. EF settings kept considering the ROT of Zone 3 Protection and studying the trend of 3Io current/fault analysis/Bus fault studies? Highset is kept disabled? |  |  |
| 14 | For 132kV Lines, OC and EF are to be kept disabled in the distance relay and enabled in the backup protection relay. The ROT of Dir. OC should be more than the Zone 2 operating time and ROT of DEF should be more than the Zone 3 operating time Highset is kept disabled? |  |  |
| 15 | Carried Aided Protection is present for the line? POTT or PUTT For short double circuit lines, Current reversal logic is enabled? |  |  |

- POWER TRANSFORMER PROTECTION

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | The transformer protection scheme present? - Main 1 and Main 2 Protection Scheme - Main and Backup Protection Scheme |  |  |
| 2 | What is the differential pickup setting for the transformers? |  |  |
| 3 | Is maximum short circuit current considered with a multiplying factor of 1.2 while considering the differential high-set/Unrestrained setting? |  |  |
| 4 | Setting for 2nd Harmonic Blocking? Setting for 5th Harmonic Blocking? |  |  |
| 5 | Is the REF Protection enabled as “High Impedance” or “Low Impedance”? Trafo#1: Trafo#2: Trafo#3: |  |  |
| 6 | In case of High Impedance REF, is the calculation of stabilizing Resistor done considering, the maximum short circuit fault current, the RCT of the CTs and the resistance of the wires? |  |  |
| 7 | At what percentage of the full load current is the overcurrent pickup kept? Trafo#1: Trafo#2: Trafo#3: |  |  |
| 8 | Is Earthfault pickup of the transformer kept at 20% of the full load current? |  |  |
| 9 | Is the Overcurrent and Earthfault Highset kept at 1.1 times the maximum short circuit current with a time delay of 50ms? |  |  |
| 10 | Is Overfluxing protection enabled? What is the alarm, pickup and Highset stage of Overfluxing protection? |  |  |
| 11 | Is the 132/33kV transformers OC and EF TMS settings calculated considering time gradient between 33kV Outgoing Feeders – Transformer LV side – Transformer HV side? |  |  |
| 12 | For 400/220kV and 220/132kV Transformers, the LV side TMS for OC is calculated considering the Zone 3 time delay of the downstream shortest line and the TMS of EF is calculated considering the DEF ROT of the downstream shortest line (or line with highest TMS) |  |  |
| 13 | Is LBB protection enabled at both HV and LV sides of transformers? |  |  |
| 14 | Mention the setting for: WTI Alarm: WTI Trip: OTI Alarm: OTI Trip: Temp. set for start of cooling system: |  |  |
| 15 | Is the condition of Silica Gel Healthy? |  |  |
| 16 | Any leakage observed in the transformer? |  |  |
| 17 | Is NIFPS installed in the transformer? |  |  |
| 18 | Notes down the following: Ambient Temperature: Dial Recorded value in the MOG: |  |  |
| 19 | The transformer inherent protections are tested periodically and found healthy |  |  |

- REACTOR PROTECTION

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | The Reactor protection scheme present? Main 1 and Main 2 Differential Protection relay with build in Backup protection Differential Protection relay and separate backup protection relays |  |  |
| 2 | What is the differential pickup setting for reactor? |  |  |
| 3 | REF Protection is High Impedance/Low Impedance? Reactor#1 Reactor#2 For High Impedance REF, it the RCT, maximum short circuit fault, wire resistance considered which setting the value of stabilizing resistor? |  |  |
| 4 | Is Harmonic Blocking enabled in the Reactor Differential Protection relay? Value of 2nd Harmonic Blocking? Value of 5th Harmonic Blocking? |  |  |
| 5 | Is backup impedance protection available for the reactor? What is the impedance reach and time delay? |  |  |
| 6 | Is backup overcurrent protection available for the reactor? What is the pickup value and the time delay? |  |  |
| 7 | Is NGR available for the reactor? If yes, what are the protection used for the NGR |  |  |
| 8 | The Reactor and NGR inherent protections are tested periodically and found healthy. |  |  |

- BUSBAR DIFFERENTIAL PROTECTION

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Is busbar differential protection present in the substation at: - 400kV Bus: - 220kV Bus: - 132kV Bus: |  |  |
| 2 | Is the scheme of Busbar differential protection Centralized or Decentralized? In case of decentralized busbar scheme, Are all the peripheral units healthy? Is the connectivity of the peripheral units to the Main Central Unit healthy? |  |  |
| 3 | Are both Check Zone and bus Zone features present? |  |  |
| 4 | Are the Status of Bus Isolators, Circuit Breakers, Line Isolators (if taken) properly reporting to the busbar relay? |  |  |
| 5 | Note down the present values from the busbar differential relay: Bus Zone A Current: Differential: Restraint: Bus Zone B Current: Differential: Restraint: |  |  |
| 6 | Is DT send logic configured in the busbar relay for transmission lines? |  |  |
| 7 | Is LBB an inbuilt feature of the busbar protection? |  |  |
| 8 | Are the feeders properly segregated among the buses (trend analysis of load and demand) so that in case of tripping of one bus bar, the other bus or feeders connected to the healthy bus is not overloaded? |  |  |

- 33kV OUTGOING FEEDER

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Non-Directional Overcurrent and Earth fault protection functions is enabled (IDTM Normal Inverse Curve) |  |  |
| 2 | Availability of Under/Over frequency, df/dt Under/Over voltage protection functions is available in the 33kV relays. (The protections are to be turned on only if there is a special case of system requirement as per studies) |  |  |
| 3 | What is the basis of Overcurrent setting? (CT Ratio or Loading of the line) |  |  |
| 4 | Is the Earthfault pickup set at 80A? (In case of lightly loaded line, is the earth fault pickup is kept keeping in view the zero-sequence current during single phase open circuit fault?) |  |  |
| 5 | Inrush/Harmonic restrained feature is enabled? |  |  |
| 6 | Highset pickup of OC and EF is kept in between 3A to 5A with a time delay of 50ms? If any other setting is kept (verify) |  |  |
| 7 | Any instance of 33kV Feeder tripping overreach a fault in the downstream distribution feeders? |  |  |
| 8 | Is the TMS for Overcurrent and Earthfault is fixed at 0.1? (Please verify if other values of TMS is set) Note: The DISCOM substations should set their TMS w.r.t grid substations |  |  |

- DISTURBANCE RECORDERS

| Sl No. | PARTICUARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Are the settings of Disturbance Recorder maintained as below: Pre-fault time: 0.5s Post-fault time: 2.5s Recording Window: 3s DR triggering Criteria: Any Start or Trip of a Protection Event |  |  |
| 2 | The DR Channels are standardized comprising of all Analog Inputs, Digital Inputs, Protection Start and Trip signals. The DR is time synchronized (As per clause No. 17 of IEGC 2023) |  |  |
| 3 | On case of any trip/fault event, the DR data is sent to Protection team within 24 hours for analysis and facilitating report uploading in the NERLDC Portal (As per Clause No. 37.2 of IEGC 2023) |  |  |

- DISCOM END PROTECTION CHECKLIST

| Sl No. | PARTICULARS | YES/NO/NA | REMARKS |
| --- | --- | --- | --- |
| 1 | Attach the SLD showing the incomer feeders from the Grid Sub-Stations, the transformers present and the 11kV Outgoing feeders emanating from the concerned Distribution Sub-Stations Note: If LILO line are available in the DSS, the same are to be shown in the SLD |  |  |
| 2 | What is the curve followed for OC and EF settings of Incomer Feeder? (IDMT normal Inverse, Very Inverse Extreme Inverse etc.) |  |  |
| 3 | What is the philosophy of TMS set in the Incomer feeder, Transformer HV and LV and 11kV Outgoing feeders? |  |  |
| 4 | Any instance recorded when the CB tripped at AEGCL end for a fault in other section of distribution lines. In that case, whether the settings were reviewed at DSS end or AEGCL end |  |  |
| 5 | Are the relays numerical or Electromechanical? (In case of electromechanical relays, please mention the same of the feeders) |  |  |
| 6 | Is DR recording feature available in the relays? |  |  |
| 7 | Are auto-reclosure functional for the lines? |  |  |
| 8 | Are the transformers CBs cut as per routine operating procedure when shutdown of incoming 33kV feeder is taken? |  |  |
| 9 | How many times the Incomer feeders have tripped in the past month? How many of them were transient fault? How many of them were permanent fault? If transient fault, what remedial measures were taken to avoid such instances of tripping in the future? |  |  |
| 10 | In case of failure of one 33kV incomer feeder, are provision for other 33kV incomer feeder available to avoid long term blackouts? |  |  |

- ANNEXURES

- SINGLE LINE DIAGRAM:

- TRANSMISSION LINE DETAILS

| A | TRANSMISSION LINES |  |
| --- | --- | --- |
| 1 | NAME OF THE LINE |  |
| 2 | CT RATIO |  |
| 3 | TOWER CONFIGURATION (SC/DC) |  |
| 4 | NAME OF CONDUCTOR USED CONDUCTOR PARAMETERS USED FOR RELAY SETTINGS: R1: R0: X1: X0: XM: RM: |  |
| 5 | LENGTH OF THE LINE |  |
| 6 | NO. OF TRIPPINGS RECORDED IN THE LAST 12 MONTHS: HOW MANY OF THEM WERE PERMANENT FAULTS (REQUIRED PHYSCIAL RECTIFICATION WORKS) |  |
| 7 | STATUS OF AUTO-RECLOSURE (ACTIVE/INACTIVE) |  |
| 8 | STATUS OF CARRIER PROTECTION (ACTIVE/INACTIVE/ABSENCE OF EQUIPMENT) IS THE PLCC THROUGH PHASE-PHASE/PHASE-GROUND/INTER-CIRCUIT COUPLING? IS CARRIER PROTECTION VIA OPGW? |  |
| 9 | IS CVT PRESENT FOR ALL PHASES? |  |
| 10 | MAXIMUM RECORDED LOAD IN THE LINE (MVA): |  |
| 11 | AVERAGE LOAD IN THE LINE IN MVA: |  |
| 12 | AVERAGE RECORDED POWER FACTOR: |  |
| 13 | ANY CONSTRAINTS APPLICABLE FOR THE LINE: |  |

- POWER TRANSFORMER DETAILS

| B | TRANSFORMERS |  |
| --- | --- | --- |
| 1 | VOTLAGE RATING |  |
| 2 | MVA RATING |  |
| 3 | %IMP AT NORMAL TAP |  |
| 4 | HV CT RATIO |  |
| 5 | LV CT RATIO |  |
| 6 | HV NCT RATIO |  |
| 7 | LV NCT RATIO |  |
| 8 | NO. OF TRIPPINGS RECORDED IN THE LAST 12 MONTHS |  |
| 9 | MAXIMUM RECORDED LOAD IN THE TRANSFORMER (MVA): |  |
| 10 | AVERAGE LOAD IN THE TRANSFORMER (MVA): |  |
| 11 | IS IT RUN IN PARALLEL: |  |
| 12 | AVERAGE RECORDED POWER FACTOR: |  |
| 13 | ANY CONSTRAINTS APPLICABLE FOR THE TRANSFORMER: |  |
| 14 | CASES OF FALSE RESTRICTED EARTH FAUTLT OPERATION IN THE LAST 12 MONTHS: CASES OF FALSE DIFFERENTIAL PROTECTION OPERATION IN THE LAST 12 MONTHS: CASES OF FALSE INHERENT PROTECTION OPERATION IN THE LAST 12 MONTHS: CASES OF DIFFERENTIAL PROTECTION OPERATION DUE TO DAMAGE OF LA |  |

- 33kV OUTGOING FEEDER DETAILS

| C | 33kV OUTGOING FEEDER |  |
| --- | --- | --- |
| 1 | NAME OF THE FEEDER |  |
| 2 | CT RATIO |  |
| 3 | NO. OF TRIPPINGS RECORDED IN THE LAST 12 MONTHS: NO. OF OC OPERATION: NO. OF EF OPERATION: |  |
| 4 | HOW MANY AMONG THEM WERE PERMANENT FAULTS (REQUIRED PHYSICAL RECTIFICATION WORKS) |  |
| 5 | MAXIMUM RECORDED LOADING IN THE LINE (MVA): |  |
| 6 | AVERAGE RECORDED LOADING IN THE LINE: |  |
| 7 | AVERAGE RECORDED POWER FACTOR: |  |
| 8 | ANY CONSTRAINTS APPLICABLE FOR THE 33kV FEEDER: |  |
| 9 | CASES OF LBB OPERATION DUE TO CB ISSUE FOR THE FEEDER: |  |