## CHAPTER 10: TECHNICAL SPECIFICATION FOR ISOLATORS (AIS)

10.0 TECHNICAL PARTICULARS OF 400 kV, 220 kV, 132 kV & 33 KV ISOLATOR are as follows:

|  | Type: | 400 kV |  |  | 220 kV | 132 kV |  | 66 kV | 33 kV |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| I | II | III |  |  | IV | V |  | VI | VII |  |
| 1 | Main switch | Centre break/Pantograph |  | Horizontal Centre break |  |  | Horizontal Centre Break | Horizontal Centre break |  | Horizontal Double break |
| 2 | Service |  | Outdoor |  |  |  |  |  |  |  |
| 3 | Applicable standard |  | IS : 9921 / IEC-62271-102 |  |  |  |  |  |  |  |
| 4 | No. of Phases |  | 3 phase |  |  |  |  |  |  |  |
| 5 | Design Ambient temperature |  | 50°C |  |  |  |  |  |  |  |
| 6 | Type of operation | Electrically Ganged |  |  | Mechanically Ganged |  |  |  |  |  |
| 7 | Rated voltage (kV) | In KV |  |  | In KV | In KV |  | In KV | In KV |  |
|  | - Nominal | 400 |  |  | 220 | 132 |  | 66 | 33 |  |
|  | - Maximum | 420 |  |  | 245 | 145 |  | 72.5 | 36 |  |
| 8 | Rated current (Amps) | 4000 |  |  | 3150 | 2000 |  | 1250 | 1250 |  |
| 9 | Short time current for 1sec.(kA) | 63 |  |  | 50 | 40 |  | 31.5 | 31.5 |  |
| 10 | Rated frequency |  | 50 HZ + 5% |  |  |  |  |  |  |  |
| 11 | System earthing |  | Effectively earthed |  |  |  |  |  |  |  |
| 12 | Temperature rise |  | As per relevant IS/IEC standards |  |  |  |  |  |  |  |
| 13 | Lightening Impulse withstand voltage (kVp) |  |  |  |  |  |  |  |  |  |
|  | (a) Across Isolating distance | 1425(+240) |  |  | 1220 | 750 |  |  | 195 |  |
|  | (b) To earth | 1425 |  |  | 1050 | 650 |  |  | 170 |  |
| 14 | 1-minute power frequency withstand voltage |  |  |  |  |  |  |  |  |  |
|  | a) Across Isolating distance | 815 |  |  | 605 | 315 |  |  | 80 |  |
|  | b) To earth | 650 |  |  | 460 | 275 |  |  | 70 |  |
| 15 | Switching Impulse withstand voltage (kVp) |  |  |  |  |  |  |  |  |  |
|  | a) Across Isolating distance | 900(+345) |  |  | - | - |  |  | - |  |
|  | b) To earth | 1050 |  |  | - | - |  |  | - |  |
| 16 | Max. RIV for frequency between 0.5MHz and 2MHz (micro-volt) | 1000 at 267kV |  |  | 1000 at 156kV | 500 at 92kV |  |  | - |  |
| 17 | Corona Extinction Voltage (kV) | 320 |  |  | - | - |  |  | - |  |
| 18 | Operating mechanism |  |  |  |  |  |  |  |  |  |
|  | a) Isolator | Motor |  |  | Motor | Motor |  | Motor | Motor |  |
|  | b) Earth switch | Motor |  |  | Motor | Motor |  | Manual | Manual |  |
| 19 | Auxiliary voltage |  |  |  |  |  |  |  |  |  |
|  | a) Control & Interlock |  | 220V DC 80% to 110% |  |  |  |  |  |  |  |
|  | b) Motor voltage |  | 3 Phase 415V AC 50Hz |  |  |  |  |  |  |  |
|  | c) Heater, lamp & socket |  | Single phase 240 V 50HZ |  |  |  |  |  |  |  |
| 20 | Safe duration of overload |  |  |  |  |  |  |  |  |  |
|  | 150% of rated current |  | 5 minute |  |  |  |  |  |  |  |
|  | 120% of rated current |  | 30 minute |  |  |  |  |  |  |  |
| 21 | Minimum creepage distance of insulator (mm) |  |  |  |  |  |  |  |  |  |
| 22 | Mounting structure | Tubular / Lattice |  |  | Tubular / Lattice | Tubular / Lattice |  | Tubular / Lattice | Tubular / Lattice |  |
| 23 | Operating time |  | Less than 12 secs |  |  |  |  |  |  |  |
| 24 | Insulator Data |  |  |  |  |  |  |  |  |  |
|  | a) Bending Strength (kgf) | 1000 |  |  | 800 | 800 |  |  | 600 |  |
|  | b) Height (mm) | 3650 |  |  | 2300 | 1500 |  | As per IS/IEC | 508 |  |
|  | c) Bottom PCD (mm) | 300 |  |  | 254 | 184 |  |  | 76 |  |
|  | d) No. of holes & hole dia. | 8x18 |  |  | 8x18 | 4x18 |  |  | 4xM12 |  |
|  | e) Top PCD | 127 |  |  | 127 | 127 |  |  | 76 |  |
|  | f) No. of holes & hole dia. | 4xM16 |  |  | 4xM16 | 4xM16 |  |  | 4xM12 |  |
|  | g) Minimum creepage distance (mm) 31mm/kV | 13020 |  |  | 7595 | 4495 |  | 2248 | 1116 |  |
| 25 | Working clearance (live part to ground) (in mm) | 8000 |  |  | 5900 | 4900 |  | As per IS/IEC | 4000 |  |
| 26 | Phase Spacing (mm.) | 6000 |  |  | 4000 | 3000 |  |  | 1500 |  |
| 27 | Minimum clearances (mm.) |  |  |  |  |  |  |  |  |  |
|  | a) Phase to Phase | 4000 |  |  | 2100 | 1300 |  |  | 320 |  |
|  | b) Phase to earth | 3500 |  |  | 2100 | 1300 |  |  | 320 |  |
|  | c) Sectional clearance | 6500 |  |  | 5000 | 4000 |  |  | 3000 |  |

- SCOPE

This specification provides for design, manufacturer, testing at manufacturer’s Works  and  delivery,  supervision  of  erection,  commissioning  (if  required)  of outdoor  station  type  400kV/220KV/132KV/  33KV,  Isolator  with/  without  earth switches,  with  electrical/mechanical  interlock,  insulators  and  complete  in  all respect with bimetallic connectors arcing horns operating mechanism, auxiliary switches, indicating devices, fixing detail etc. as described hereinafter.

  - STANDARDS

Disconnecting switches covered by this specification shall conform to latest edition IEC-129/IEC 62271-102 I.S.1813 and IS: 9921, IS-325 and unless specifically stated otherwise in this specification.

10.2	TYPE

The 400,220&132 KV Isolators shall be outdoor type with centre break type/Pantograph type as required  [Single(SI)/ Double(DI)] Isolators suitable for electrical as well as manual operation and local/ remote operation; but 33KV Isolators (SI or DI) shall be outdoor type with three phase double break center rotating manual as well as motor operated type with local/remote operation. They shall have crank and reduction gear mechanism.

All Isolators offered shall be suitable for horizontal upright mounting on steel structures. Each pole unit of the multiple Isolators shall be of identical construction and mechanically linked for gang operation.

Each pole of the Isolator shall be provided with two sets of contacts to be operated in series and the moving contact blades shall rotate in horizontal plane.

The design shall be such that the operating mechanism with the linkages shall be suitable for mounting on any of the outer pole ends without much difficulty and with minimum shifting of parts.

Moving contacts of all isolators shall rotate through 90 deg. from their “fully closed position” to “fully open position so that the break is distinct and clearly visible from ground level.

The Isolators offered by the Bidder shall be designed for Normal rating current for Isolator as follows:

| 400kV | 220kV | 132kV | 66kV | 33kV |
| --- | --- | --- | --- | --- |
| 4000A | 3150A | 2000/1600/1250A | 2000/1250A | 2500/1600/1250A |

It should suitable for continuous service at the system voltages specified herein. The Isolators shall be suitable to carry the rated current continuously and full short circuit current of 63/50/40/31.5 KA for 400/220/132/33 KV respectively for 3 second at site condition without any appreciable rise in temperature. These shall also be suitable for operation at 110% rated (normal) voltage. The Isolators shall be suitable for Isolating low capacitive / inductive currents of 0.7amp at 0.15 power factor. The isolators shall be so constructed that they don’t open under the influence of short circuit conditions.

The Isolators and earthing switches are required to be used on electrically exposed installation and this should be taken into account while fixing the clearance between phases and between phase and earth. so that de-energized isolator and earth switch also can be manually operated when the parallel

circuit is energized.

10.3	MAIN CONTACTS

All Isolators shall have heavy duty, self-aligning and high-pressure line type dust-free  jaw contacts made of high conductivity, corrosion resistant, hard-drawn electrolytic copper strips of proper thickness and contact area. Fixed contact should consist of loops of above copper strips suitable for 4000 Amps, 3150 Amps, 2000 Amps, and 1250Amps ratings for 400kV, 220 KV, 132KV and 33KV Isolators respectively. The hard dawn electrolytic copper strips should be silver plated 25micron thickness and fixed contacts should be backed by powerful phosphor bronze/stainless steel springs of suitable numbers. The main contacts should be preferably of tulip type design. However, the thickness and contact area of the contact should conform to the drawing approved during type test. Moving contact with moving arm should be of hard- drawn electrolytic copper of proper thickness and contact area.

These fixed and moving contacts shall be able to carry the rated current continuously and the maximum fault current of 63/50/40/31.5 KA for 400/220/132/33KV respectively for 3 seconds without any appreciable rise in temperature. The Isolator blades shall retain their form and straightness under all conditions of operation including all mechanical stress arising out of operation as well as under rated short circuit condition.

Fixed  guides  shall  be  provided  so  that  even  when  the  blades  are  out  of alignment,  closing  of  the  switches,  proper  seating  of  the  blades  in  between contacts and adequate pressure to give enough contact surface is ensured. The contact shall be self-cleaning by the wiping action created by the movements of the blades.

The Isolator shall be self-cleaning type so that when isolators remain closed for long periods in a heavily polluted atmosphere, binding does not occur. No undue wear or scuffing shall be evident during the mechanical endurance tests, contacts and springs shall be designed so that adjustment of contact pressure shall not be necessary throughout the life of the isolator. Each contact or part of contacts shall be independently sprung so that full pressure is maintained on all contact at all times.

10.4	ARCING HORN AND GRADING HORN

Suitable arcing horn made of tinned electrolytic copper which are required for guiding contacts shall be provided on the fixed and moving contacts of all Isolators. The contacts shall be of ‘make before and break after” type. Aluminium  alloy  grading  ring  are  to  be  provided  for  220kV  and  above voltage level.

10.5	ELECTRICAL INTERLOCK / MECHANICAL INTERLOCK

The disconnecting switches whenever required shall be with an approved type electrical interlock for interlocking with the associated circuit breakers and earth switch.

Electrical interlock shall ensure reliable operation. The design should be such  that  the  electrical  circuit  for  the  interlocking  mechanism  will  remain energised as per operation of the isolator with integrated earth switches.

10.6.	AUXILIARY SWITCHES

All isolators and earthing switches shall be provided with 220VDC auxiliary switches for their remote position indication on the control board and for electrical locking with other equipment. The auxiliary switch shall be provided with a minimum of six auxiliary contacts- 10 normally open and 10 normally closed and 10 normally open and 10 normally closed for earth switch. Separate auxiliary switches shall be provided for isolating and earth switches. 6 additional NO and NC contact to be provided as spare in each case.

The auxiliary switches and auxiliary circuits shall have a continuous current carrying capacity of at least 10 Amps. Auxiliary switches shall not be used as limit switches. Details of make, rating and type of limit switch shall be furnished in the offer.

10.7	EARTH SWITCH

Line earth switch shall consist of three earthing blades for Isolator which normally rest against the frame when the connected Isolator is in closed position. The earthing blades for three phases shall be mechanically linked to a coupling shaft which shall be capable of being fitted on either side of the Isolator. The earthing blades shall match and be similar to the main switch blades and shall be provided at the hinge; with suitable flexible conductors with terminal lugs for connecting to the station ground bus. The earthing blades shall be operated by a separate mechanism but shall be mechanically interlocked with the main switch so that the earthing blades can be closed only when the main switches are in open position and vice-versa. The earthing blades shall be gang operated and all the three blades will operate simultaneously.

10.8	OPERATING MACHANISM

The operating mechanism shall be simple and shall ensure quick and effective 10000 mechanical operation. The design shall be such as to enable one man to operate it with nominal effort. The operating mechanism box shall be made out of aluminium extruded (Aluminium alloy) sections of minimum 3.0 mm thickness. The operating mechanism shall be strong rigid and not subject to rebound.

The Isolator blades shall be in positive continuous control throughout the entire cycles  of  operation.  The  operating  rods  and  pipes  shall  be  rigid  enough  to maintain positive control under most adverse conditions and to withstand all torsional and bending stresses arising from operation. Operation of the switches at any speed should not result in improper functioning, in displacement of parts / machines after final adjustment has been made. All holes in cranks, linkages etc. having moving pins shall be fitted accurately so as to prevent slackness and lost motion.

Provision shall be made for padlocking the operating mechanism of disconnecting and earth switches in both open and closed positions.

Bearings shall be ball and roller type shall be protected from weather and dust by means of cover and grease retainers. Bearings pressures shall be kept low to ensure long life and care of operation.

Each  power  operated  isolator  shall  be  motor  driven  as  well  as  manually operated and shall be complete with local / remote selector switch and open /close push buttons.

Provision shall be made in the control cabinet to disconnect power supply to prevent local / remote power operation. Limit switches shall be provided with required number of contacts for isolators and earth switches.

All the terminal blocks to be used in the operating mechanism should of Ring type of Poly-amide/Melamine material of make like Elmex/Connectwell.

10.9	DESIGN, MATERIALS AND WORKMANSHIP

The live parts shall be designed to eliminate sharp points, edges and corona producing  surfaces.  Where  this  is  impracticable,  adequate  shields  to  be provided. All ferrous metal parts shall be hot dip galvanized, as per IS 2629.All metal parts shall be of such materials or treated in such a way so as to avoid rust, corrosion and deterioration due to continued exposure to atmosphere and rain. All current carrying parts shall be made from high conductivity electrolytic copper .

Bolts, screws and pins shall be provided with standard locking device viz. Locknuts, spring washers, keys etc. and when used with current carrying parts, they shall be made of copper silicon or other high conductivity and wear resistant alloys.

The  isolators  should  not  need  lubrication  of  any  parts  except  at  very  long interval of five year minimum.

10.10 PROTECTIVE COATINGS

All ferrous parts including bolts, nuts and washers of the switches assembly shall be galvanized to withstand at least six one minute dips in copper sulphate solution of requisite strength (Prece tests) except the threaded portions which should withstand four dips.

10.11 INSULATORS

Support  insulators  for  all  type  of  isolators  shall  be  of  solid  core  type.  The insulator  shall  be  made  of  homogeneous  and  vitreous  porcelain  of  high mechanical and dielectric strength. It shall have sufficient mechanical strength to sustain electrical and mechanical loading on account of wind load, short circuit, seismic forces etc. Glazing of the porcelains shall be of uniform dark brown colour with a smooth surface arranged to shed away raise water. The porcelain shall be free from laminations and other flaws or imperfections that might affect the mechanical or dielectric quality. It shall be thoroughly vitrified, tough and impervious to moisture. The porcelain and metal ports shall be assembled in such a manner and with such material that any thermal differential expansion between  the  metal  and  porcelain  parts  throughout  the  range  of  temperature specified in this specification shall not loosen the parts or create under internal stresses which may affect the mechanical or electrical strength or rigidity. The assembly shall not have excessive concentration of electrical stresses in any section  or  across  leakage  surfaces.  The  cement  used  shall  not  give  rise  to chemical reaction with metal fittings. The insulator shall be suitable for water washing by rain or artificial means in service condition. Profile of the insulator shall also conform to IEC-815. Caps to be provided on top of the insulator shall be of high-grade cast iron or malleable steel casting. It shall be machine faced and  hot  dip  galvanized.  The  cap  shall  have  four  numbers  of  tapped  holes spaced on a pitch circle diameter of 127mm. The holes shall be suitable for bolts with threads having anti corrosive protection. The effective depth of threads shall not be less than the nominal diameter of the bolt. The cap shall be so designed that it shall be free from visible corona and shall have radio interference level as specified in table  of Clause 10.0  of Casing shall be free from blow holes cracks and such other defects.

10.12	 CONTROL CABINET:

The control cabinet of the operating mechanism shall be made out of minimum 3mm thick aluminium alloy sheet. Hinged door shall be provided with pad locking arrangement. Sloping rain hood shall be provided to cover all sides. 15 mm thick neoprene or better type of gaskets shall be provided to ensure degree of protections of at least IP 55 as per IS 2147/IS-3947. The cabinet shall be suitable for mounting on support structure with adjustment for vertical, horizontal and longitudinal alignment. Details of these arrangements shall be furnished along with the offer.

10.13	 MOTOR:

Motors rated 0.5 KW and above shall be provided with suitable for operation on 3 phase, 415 V, 50 Hz supply. Motors of lower rating shall be single phase type suitable for 240V, 50Hz system. It shall be totally enclosed type if mounted outside the control cabinet. The motor shall withstand without damage stalled torque for at least 3 times the time lag of the tripping device. The motor shall, in all other respects, conform to the requirement of I.S. 325. Suitable relay/device shall  be  provided  to  prevent  over  loading  of  the  motor.  Single  phase preventer  (for  3  phase  meter)  shall  be  provided  to  operate  on  open circuiting of any phase and shall trip off the motor. Complete details of the devices shall be furnished in the offer.

10.14	 GEAR:

The  dis-connector  /  isolator  may  be  required  to  operate  occasionally,  with considerably  long  idle  intervals.  Special  care  shall  be  taken  for  selection  of material for gear and lubrication of gears to meet this requirement. The gear shall be made out of aluminium bronze or any other better material lubricated for life with graphite or better-quality non-drawing and non-hardening type grease. Wherever necessary automatic relieving mechanism shall be provided.

10.15 SPACE HEATERS:

Space heaters suitable for 1 phase 240V AC supply shall be provided for each motor operated operating mechanism to prevent condensation and shall be operated by MCB.

10.16 TERMINAL BLOCK AND WIRINGS

Each  operating  mechanism  shall  be  provided  with  1100V  grade  ring  type terminal  block.  All  auxiliary  switches,  spare  contact  of  the  contactors, interlocks and other terminals shall be wired up to terminal block. The terminal block shall have at least 20% extra terminals. All wiring shall be carried out with 1.1KV grade PVC insulated 2.5 sq.mm. copper wires.

10.17 INTERIOR ILLUMINATION:

A holder suitable for a 240 V lamp shall be provided in each of the motor operated mechanism of three poles & shall be door operated type.

10.18 CONTROL AND AUXILIARY SUPPLY:

A 3-phase switch with MCB for phases and link for neutral, shall be provided for power supply and a 2 pole MCB shall be provided for control supply.

10.19 POSITION INDICATOR:

A position indicator to show the isolator is in ON or OFF position to be provided.

10.20 NAME PLATE:

Isolator, earthing switches and their operating devices shall be provided with name plate. The name plate shall be weatherproof and corrosion proof. It shall be mounted in such a position that it shall be visible in the position of normal service and installation. It shall carry the following informations duly engraved or punched on it.

- Isolator Base

Name: AEGCL

Name of manufacturer –

Order No. –

Type Designation –

Manufacturers serial No. –

Rated voltage –

Rated normal current –

Rated short time current (rms) and duration –

Rated short time peak current (KAP)

Weight-

Manufacturing Statndard-

B.  Earthing Switch

Name: AEGCL

Name of manufacturer –

Order No. –

Type Designation –

Manufacturers serial No. –

Rated voltage –

Rated normal current –

Rated short time current (rms) and duration

Rated short time peak current (KAP)

Weight

- Operating Device

Name – AEGCL

Name of manufacturer –

Order No.

Type Designation –

Reduction gear ratio –

AC motor

i)	Rated auxiliary voltage

ii)	Starting current

iii)	Designation of AC motor as per IS 4722/325

iv)	Starting torque at 80% of supply voltage

v)	Over travel in degrees after cutting off supply

Total operating time in seconds

i)	Close operation – Electrical

ii)	Open operation – electrical

iii) Open operation – manual

10.21 PAINTING GALVANIZING AND CLIMATE PROOFING:

At interiors and exteriors of enclosures, cabinets and other metal parts (other than made up of aluminium) shall  be thoroughly cleaned to remove all rust, scales, corrosion, grease and other adhering foreign matter and the surfaces treated  by  phosphating  (e.g.  seven  tank  phosphating  sequence).  After  such preparation of surfaces, two coats of zinc oxide primer shall be given by suitable stoving and air drying before final painting with epoxy paint. Colour of the final paints shall be of shade no. 697 of IS:5. The finally painted cubicle shall present aesthetically pleasing appearance free from any dent or uneven surface.

Paint inside the metallic housing shall be of anti-condensation type and the paint on outside surfaces shall be suitable for outdoor installation.

All components shall be given adequate treatment of climate proofing as per IS:3202 so as to withstand corrosive and severe service conditions.

All metal parts not suitable for painting such as structural steel, pipes, rods, levers, linkages, nuts and bolts used in other than current path etc. shall be hot dip galvanized as per IS –2629. Galvanization test will be carried out during routine test.

Complete details of painting, galvanizing and climate proofing of the equipment shall be furnished in the offer.

10.22 TESTS:

Type Tests:

Isolators offered, shall be fully type tested as per the relevant standards. The Bidder shall furnish Three sets of the following valid type test reports for their different type of offered Isolators along with the offer. The AEGCL reserves the right  to  demand  repetition  of  some  or  all  the  type  tests  in  the  presence  of AEGCL’s representative. For this purpose, the Bidder may quote unit rates for carrying out each type test and this will be taken during bid price evaluation, if required.

a)    short time withstand & peak withstand current test for Isolator & Earth Switch.

b)   power frequency (Dry & Wet), Lightening Impulse dry withstand Test

c)    Mechanical endurance Test

d)    IP-55 test

e)    Seismic test

f)    Temperature Rise test

During type tests the isolator shall be mounted on its own support structure or equivalent support structure and installed with its own operating mechanism to make the type tests representative. Drawing of equivalent support structure and mounting arrangements shall be furnished for Purchaser’s approval before conducting the type tests.

The type tests shall be conducted on the isolator along with approved insulators and terminal connectors. Mechanical endurance test shall be conducted on the main switch as well as earth switch of one isolator of each type.

Acceptance and Routine Test:

All acceptance and routine test as stipulated in the relevant standards shall be carried out by the supplier in presence of Purchaser’s representative.

Mechanical operation test (routine test) shall be conducted on isolator (main switch and earth switch) at the supplier’s works as well as purchaser’s substation site.

Immediately after finalization of the programme of type / acceptance, routine testing  the  supplier  shall  give  sufficient  advance  intimation  (clear  20  days advance intimation), along with shop routine test certificates, valid calibration reports from Govt. approved (NABL) test house for the equipment, instruments to be used during testing for scrutiny by the AEGCL to enable him to depute his representative for witnessing the tests. If there will be any discrepancies in the shop routine test certificates and calibration reports furnished by the firm then after  settlement  of  the  discrepancies  only,  purchaser’s  representative  will  be deputed for witnessing the tests. Special tests proposed to be conducted (if decided to conduct) as type test on isolators, are given at Annexure- II. Thesespecial type test charges shall be quoted along with all other type tests as per relevant IEC standard and these charges shall be included in the total bid price

Test certificates of various items including but not limited to the following shall be furnished at the time of routine tests.

a)	Chemical analysis of copper along with a copy of excise certificate indicating genuine source of procurement of electrolytic grade copper.

b)	Bearings

c)	Fasteners

d)	Universal / swivel joint coupling

e)	Insulators

f)	Motor

g)	Gears

h)	Auxillary switch

i)	Limit switch

j)	Timer

k)	Overload / single phase preventer relay

l)	Interlocking devices

m)	Terminal block

n)	Any other item

10.23 INSPECTION:

i)	The Purchaser shall have access at all times to the works and all other places of manufacture, where the disconnectors, earth switches and associated equipment are being manufactured and the supplier shall provide all facilities for unrestricted inspection of the works  raw materials manufacture of  all the accessories and for conducting necessary tests as detailed herein.

ii)	The supplier shall keep the purchaser informed in advance of the time of starting of the progress of manufacture of equipment in its various stages so that arrangements could be made for inspection.

iii)	No material shall be dispatched from its point of manufacture unless the material has been satisfactorily inspected and tested.

iv)	The acceptance of any quantity of the equipment shall in no way relieve the supplier of his responsibility for meeting all the requirements of this specification and shall not prevent subsequent rejection if such equipment is later found to be defective.

10.24 QUALITY ASSURANCE PLAN:

The Bidder shall invariably furnish following information along with his offer, failing which his offer shall be liable for rejection.

(i)	Names of sub suppliers for raw materials, list of standards according to which the raw materials are tested, list of tests normally carried out on raw materials in presence of Supplier’s representative, copies of test certificate

(ii)	Information and copies of test certificates as in (i) and (ii) above in respect of bought out accessories.

(iii)	List of manufacturing facilities available

(iv)	Level of automation achieved and lists of areas where manual processing still exists.

(v)	List of areas in manufacturing process, where stage inspections are normally carried out for quality control and details of such tests and inspections.

(vi)   List   of   testing   equipment   with   calibration   certificates   from   Govt. approved(NABL) test house available with supplier for final testing equipment and test plant limitation if any, vis-à-vis the type, special acceptance and routine test specified in the relevant standards. These limitations shall be very clearly brought out in the specified test requirements.

(vii) QAP shall include acceptance criteria mentioning clause no. of applicable standard against each parameter.

The supplier shall within 30 days of placement of order, submit following information to the purchaser.

i)	List of raw material as well as bought out accessories and the names of sub-suppliers selected from the lists furnished along with offer.

ii)	Type test certificates of the raw material and both bought out accessories.

iii)	Quality Assurance Plan (QAP) withhold points for purchaser’s inspection.

The supplier shall submit the routine test certificates of bought out accessories and raw material viz. Copper, aluminum conductors, lubricating material, gear material etc. at the time of routine testing of the fully assembled isolator.

10.25 DOCUMENTATION:

All  drawings  shall  conform  to  relevant  international  standards  organization (ISO).. All dimensions and data shall be in S.I. Units.

List of Drawings and Documents

The Bidder shall furnish four sets of following drawings / documents along with his offer.

a)   General   outline  and  assembly  drawings  of  the  dis-connector operating    mechanism,    structure,    insulator    and    terminal connector.

b)    Sectional views and descriptive details of items such as moving blades, contacts, arms contact pressure, contact support bearing housing of bearings, balancing of heights, phase coupling pipes, base   plate,   operating   shaft,   guides,   swivel   joint   operating mechanism and its components etc.

c)     Loading diagram

d)    Drawings with structure for the purpose of type tests.

e)     Name plate.

f)     Schematic drawing.

g)    Type test reports.

h)    Test  reports,  literature,  pamphlets  of  the  bought-out  items  and raw material.

i)     Deviation sheet/compliance sheet if applicable

Six sets of the type test report, duly approved by the Purchaser shall be submitted by the supplier for distribution, before commencement of supply Adequate copies of acceptance and routine test certificates, duly approved by the Purchaser shall accompany the dispatched consignment.

The manufacturing of the equipment shall be strictly in accordance with the approved drawings and no deviation shall be permitted without the written approval of the purchaser. All manufacturing and fabrication work in connection with the equipment prior to the approval of the drawing shall be at the supplier risk.

The supplier shall within 2 weeks of placement of order submit four sets of final versions of all the above said drawings for AEGCL’s approval. The purchaser shall communicate his comments / approval on the drawings to the supplier. The supplier shall, if necessary, modify the drawings and resubmit four copies of the modified  drawings  for  AEGCL’s  approval  within  two  weeks  from  the  date  of comments.

10.26 INSTRUCTION MANUALS:

Fifteen copies of the erection, operation and maintenance manuals in English to be supplied for each type of disconnector one month prior to dispatch of the equipment. The manual shall be bound volumes and shall contain all drawings and information required for erection, operation and maintenance of the disconnector including but not limited to the following particulars.

(a)	Marked erection prints identifying the component parts of the disconnector as shipped with assembly drawings.

(b)	Detailed dimensions and description of all auxiliaries.

(c)	Detailed views of the insulator stacks, metallics, operating mechanism, structure, interlocks, spare parts etc.

10.27 PACKING AND FORWARDING:

The equipment shall be packed in crates suitable for vertical / horizontal transport, as the case may be and suitable to withstand handling during transport and outdoor storage during transit. The supplier shall be responsible for any damage to the equipment during transit, due to improper and inadequate packing. The easily damageable material shall be carefully packed and marked with the appropriate caution symbols.

Wherever necessary, proper arrangement for lifting, such as lifting hooks etc. shall be provided. Any material found short inside the packing cases shall be supplied by supplier without any extra cost.

Each consignment shall be accompanied by a detailed packing list containing the following information:

(a)	Name of the consignee.

(b)	Details of consignment.

(c)	Destination.

(d)	Total weight of consignment.

(e)	Handling and unpacking instructions.

(f)	Bill of material indicating contents of each package.

The supplier shall ensure that the bill of material is approved by the purchaser before dispatch.

10.28 SUPERVISION OF ERECTION TESTING AND COMMISSIONING (ET&C):

Purchaser proposes to utilize the services of the supplier for supervision of testing and commissioning of the equipment being supplied by him, if it is required. For this purpose, the supplier should make available the services of trained personnel (Engineers) who shall correct in the field, any errors or omissions in order to make the equipment and material properly perform in accordance with the intent of this specification. The Engineer shall also instruct the plant operators in the operation and maintenance of the commissioned equipment. The supplier shall be responsible for any damage to the equipment on commissioning the same, if such damage results for the faulty or improper ET&C. Purchaser shall provide adequate number of skilled / semi-skilled workers as well as ordinary tools and equipment and cranes required for equipment erection, at his own expenses. Apart from the above, the Purchaser shall not be responsible for providing any other facilities to the supplier. Special tools if required for erection and commissioning shall be arranged by the supplier at his cost and on commissioning these shall be supplied to the purchaser free of cost for future use.

APPENDIX – I

(Isolators)

LIST OF SPECIAL TESTS TO BE CARRIED OUT IF DECIDED BY THE PURCHASER

| Sl. No. | Name of the Test | Standard to which it conforms. |
| --- | --- | --- |
| 1. | Test for visible Corona and Radio interference voltage (RIV) on disconnectors and terminal connector | NEMA Pub No. 107-1964 ISRI Pub No. 1-1972 |
| 2. | Tests on insulators | IS-2544 IEC. 168 |
| 3. | Tests on terminal connectors | IS:5561 |
| 4. | Tests on galvanized components | IS:2633 |
| 5. | Stalled torque test on motor operating mechanism | At 110% of supply voltage |