CHAPTER 20: TECHNICAL SPECIFICATION FOR XLPE CABLE WITH TERMINATION

# TECHNICAL SPECIFICATION OF 33kV, 66KV, 132KV, 220KV & 400KV XLPE CABLE AND TERMINATION

### 20.1 	SCOPE

#### The specification covers Design, Engineering, Construction, Supply & Delivery, Erection, Laying, Testing & Commissioning including Transportation & Insurance, Storage of XLPE Cable of different ratings and their associated works.

### 20.2 	STANDARD & CODES

#### The works covered by the specification shall be designed, engineered, manufactured, tested and commissioned in accordance with the Standards as specified in the table below.

Other internationally accepted standards which ensure equivalent or better performance than that specified in the standards referred shall also be accepted. Copies of such standards shall be submitted by the bidder along with the bid.

| IS 7098 : Part 3 : 1993 |  | Cross-linked polyethylene insulated thermoplastic sheathed cables: For working voltage from 66KV up to and including 220KV. |  |
| --- | --- | --- | --- |
| IS 8130 : 1984 |  | Conductors for insulated electric cables and flexible cords |  |
| IS 5831 : 1984 |  | PVC insulation and sheath of electric cables. |  |
| IS 1255 : 1983 |  | Code of practice for installation and maintenance of power cables upto and including 33KV rating. |  |
| IS 3975 : 1999 |  | Mild steel wires, formed wires and tapes for armouring of cables. |  |
| IS 5831 : 1984 |  | PVC insulation and sheath of electric cables. |  |
| IS 6380 : 1984 |  | Elastomeric insulation and sheath of electric cables. |  |
| IS 8130 : 1984 |  | Conductors for insulated electric cables and flexible cords. |  |
| IS10418 : 1982 |  | Drums for electric cables |  |
| IS 5 : 1994 |  | Colours for ready mixed paints and enamels. |  |
| IS 617 : 1994 |  | Aluminum and aluminium alloy ingots and castings for general engineering purposes (Superseded IS 20: 1977) |  |
| IS 3043 : 1987 |  | Code of practice for earthing. |  |
| IS 5578 : 1984 |  | Guide for marking of insulated conductors. |  |
| IS 11353 : 1985 |  | Guide for Uniform System of Marking and Identification of Conductors and Apparatus Terminals. |  |
| IS 5216 : Part I : 1982 |  | Recommendations on Safety Procedures and Practices in Electrical Work. |  |
| IS 2071 : 1993 |  | High voltage test techniques. |  |
| IEC-60540 |  | Power cables with extruded insulation and their accessories and cords |  |
| EC 60060 : 1989 |  | High Voltage Test Techniques |  |
| IEC-60502 |  | Extruded solid dielectric insulated power cables for rated voltages from 1KV up to 30KV |  |
| IEC-60754 : 1991 |  | Tests on gases evolved during combustion of electric cables |  |
| IEC-60183 : 1990 |  | Guide to the Selection of High Voltage Cables. |  |
| IEC-60230 : 1996 |  | Impulse tests on cables and their accessories. |  |
| IEC-60840 / IEC- 62067 |  | Testing |  |
| IEC-60287 : 1995 |  | Calculation of the continuous current rating of cables (100%load factor). |  |
| IEC-60304 : 1982 |  | Standard colours for insulation for low-frequency cable and wires |  |
| IEC-60331 : 1970 |  | Fire resisting characteristics of Electric cables. |  |
| IEC-60332 : 1992 |  | Tests on electric cables under fire conditions. |  |
| BS-5468 |  | Cross-linked polyethylene insulation of electric cables |  |
| IEC-60228 : 1978 |  | Conductors of insulated cables |  |
| IEC-60332 : 1993 |  | Test on electric cables under fire conditions |  |
| IEC-60066 |  | Environmental Test |  |
| IEC-60117 |  | Graphical Symbols |  |
| IEC-60270 : 2000 |  | Partial Discharge Measurements |  |
| CSA-Z299.1-1978h |  | Quality Assurance Program Requirements |  |
| CSA-Z299.2-1979h |  | Quality Control Program Requirements |  |
| CSA-Z299.3-1979h |  | Quality Verification Program Requirements |  |
| CSA-Z299.4-1979h |  | Inspection Program Requirements |  |
| ASTMD-2863 |  | Measuring the minimum oxygen concentration to support candle like combustion of plastics (oxygen index) |  |

20.3      COMPLIANCE TO SPECIFICATION & DEVIATION:

Normally the offer should be as per Technical Specification without any deviation. But any deviation felt necessary to improve performance, efficiency and utility of equipment must be mentioned in the Deviation Schedule with reasons duly supported by documentary evidence. Such deviations suggested may or may not be accepted by the purchaser.

As a mark of technical conformance, all sheets of the specification shall be furnished by each bidder with the signature and company seal affixed thereon. In case of any deviations, the same shall be carried out in the deviation schedule only. Deviations not mentioned in Deviation schedule will not be considered.

The bidder shall also submit the GTP as per Annexure-1 duly signed with date & company seal for acceptance of the Technical Bid unless which the bid may be considered as non-responsive.

20.4	CONSTRUCTION

    - For 66KV and above: The cable shall be of applicable EHV grade as per  requirement  according  to  price  schedule,  single core,  armored, stranded  compacted  circular  Copper  conductor  in  case  of  cross section  less  than  or  equals  to  800  sq.mm  or  segmental  compacted circular (Miliken) Copper conductor in case of cross section over 800 sq.mm, core screening by a layer of semiconducting tape followed by a   layer   of   semiconducting   compound,   crosslinked   polyethylene (XLPE)   tree-   retardant/   super   clean   dry   cured   insulation, insulation   screening   with    semiconducting   compound    extruded directly  over  the  insulation,  longitudinal  sealing  by  a  layer  of  non woven  tape  with  water  swellable  absorbent  over  insulation  screen, followed  by  radial  sealing  of  corrugated  &  seamless  aluminum& overall  HDPE  sheathed  (conforming  to  IEC  60840/  IS  7098  Part III)& graphite coated and conforming to the technical particulars of specification.

For 33KV : Untinned annealed copper  conductor  of  class  2  as  per  IS  8130/1984  and  any  latest amendments  to  it.  The  shape  of  conductor  shall  be  compacted, stranded,  and   circular/   sector  shaped,  shielded  with  conductor screen   of   black   extruded   semi-conducting   compound   ,   XLPE insulation,  shielded  with  insulation  screen  of  black  extruded  semi- conducting   compound,   black   semi-conducting   tape   and   metallic screen  of  copper  tape,  Inner  sheath  extruded  PVC  type  ST2,  single layer   of   strip/   round   steel,   round   hard   drawn   aluminium   wire armoured and black extruded FR-PVC (TypeST-2) overall sheathed, conforming generally to IS:7098 (PartII

20.5	COMPOSITIONS OF CABLES

  - CONDUCTOR

For  the  cable  sizes  having  cross  section  over   800 sq.mm,  the segmental  compacted  circular  conductor  having  minimum  four  (4) segments should be constructed for the supply under the scope of bid. When  the  conductor’s  cross-section  is  less  than  400  sq.mm,  the compacted circular is applied generally.

  - CONDUCTOR SCREEN

The conductor screen shall consist of extruded semi-conducting XLPE. Semi-conducting separator tapes may be applied between conductor and the extruded semi-conductor XLPE.

  - INSULATION

The  insulation  material  shall  be  extruded  cross-linked  polyethylene for  33kV  and  tree-  retardant/  super  clean  XLPE  for  66kV  and above.. In order to ensure that the screen and insulation are intimately bonded together and free from all possibilities of voids between layers, the conductor screen, the insulation and the insulation screen should be extruded simultaneously in one process in single cross-head. The extrusion process should be carried out under strictly controlled atmospheric conditions.

The thickness of the insulation layer should be maintained as the maximum value figured out from the design of the impulse voltage and A.C. voltage. The cross-linking process by N2 gas should be preferred instead of conventional cross-linking process by saturated steam.

  - INSULATION SCREEN

The insulation screen shall consist of extruded semi-conducting XLPE. Suitable bedding tapes shall be applied over the extruded semi-conducting XLPE.

  - MOISTURE BARRIER

The longitudinal water barrier shall be applied over insulation screen by a layer of non woven synthetic tape with suitable water swellable absorbent.

  - METALLIC SCREEN:

The   metallic   screen   shall   be   of   copper   wire   or   corrugated aluminium as per IS. The metallic screen shall be designed to meet the requirement of the system short circuit rating of 31.5KA for 3 sec (for 33KV and 66KV), 40KA for 3Sec (for 132KV) and 50KA for 3 sec (for 220KV). Copper wire screening may be used if required to meet the above ratings.

ARMOURING (FOR 33KV CABLE)

    - The armoring shall be of non-magnetic material.

    - Armoring shall be applied over the insulation or protective barrier or non-metallic part of insulation screening, in case of single core cables or inner sheath in case of screened and armoured single core cables.

c)    The armour wires/strips shall be applied as closely as practicable the direction of lay of the armour shall be left hand. For double wires/strips armoured cables, this requirement shall apply to the inner layer of wires/strips. The outer layer shall, except in special cases, be applied in the reverse direction to the inner layer, and there shall be a separator of suitable non-hygroscopic material; such as plastic tape, bituminized cotton tape, bituminized hessian tape, rubber tape, proofed tape between the inner and outer layers of armour wires strips.

d)     A binder tape may be applied on the armour.

e)   The joints in armour wires of strips shall be made by brazing or welding and the surface irregularities shall be removed. A joint in any wire/strip shall be at least 300 mm from the nearest joint in any other armour wire/strip in the completed cable, Number of joint in a single wire to be limited.

### OUTER SHEATH

The outer sheath shall consist of Extruded black HDPE (TypeST7) grade. The outer sheath shall be designed for protection against termite and rodent attack and shall be coated with graphite.

20.6	RATING

A complete set of calculation made in arriving at  the current rating shall  be  furnished  for  laying  condition  and  cable  sheath  bonding system adopted. Short circuit temperature shall be limited to 250 degree C.

20.7	CABLE DRUMS

Cables shall be supplied in wooden or steel drums of heavy construction of suitable size and packed conforming to IS 10418 or applicable internationally accepted standards. Wooden drum shall be properly seasoned sound and free from defects. Wood preservative shall be applied to the entire drum. A layer of water proof paper shall be applied to the surface of the drums and over the outer most cable layer.

Each drum shall carry the manufacturer’s name, the purchaser’s name, address and contract number and type, size and length of the cable, net and gross weight stenciled on both sides of drum. A tag containing the same information shall be attached to the leading end of the cable. A narrow and suitable accompanying wording shall be marked on one end of the reel indicating the direction in which it should be rolled.

Packing shall be sturdy and adequate to protect the cables, from any injury due to mishandling or other conditions encountered during transportation, handling and storage. Both cable ends shall be sealed with hermetically sealed by means of water blocking compound followed by heat shrinkable caps totally coated inside with mastic so as to prevent to cable for moisture penetration during transit, storage and laying.

The bidder shall consider supply of cable on returnable drums basis. Contractor shall take back all the cable drums from site after successful laying, testing and commissioning of cables. If any length of cable remains unused, the same shall be adjusted by the employer.

  - Embossing of outer sheet: the following details on the other sheet of cable at a regular interval of 1(one) meter.

    - Name of Customer i.e. AEGCL

    - Conductor size, type of insulation and voltage grade.

    - Manufacturer’s name.

    - Year of manufacturing

20.8	TESTS

All routine and acceptance tests shall be conducted as per IEC60840/IEC62067. All type tests conducted during last five years from the date of NIT as per IEC 60840:1999/ IEC 62067:2001 including its amendments on the XLPE insulated HT cable should be submitted. The diameter of test cylinder during bending test shall be as per IS:7098 (Part3) or the diameter of drum barrel to be used for dispatch of cables which ever is lower. For accessories type test reports should be submitted as per Clause 11.3.2 IEC 60840:1999/ Clause12.4.2 IEC62067:2001 & including amendments.

Following additional type tests shall be carried out on outer sheath of XLPE insulated HT cable.

- Oxygen index and temperature index test as per ASTMD-2863.

- Chemical composition test for verifying lead sheath composition.

All tests as prescribed in IEC-60840 shall be performed after installation of cable.

TESTS AFTER INSTALLATION

All tests as prescribed in IEC-60840:1999/IEC 62067:2001 shall be performed after installation of cable.

20.9	TRENCHING

The cable trench work involves earth excavation for cable trench, back filling and removal of excess earth from site. The work site shall be left as clean as possible.

The trench shall be excavated using manual/ mechanical modes as per field conditions.

Where paved foot paths are encountered, the pavements labs shall be properly stored and reinstated. Identification markers of other services shall be properly stored and restored.

The sides of the excavated trenches shall wherever required be well shored up.

Suitable barriers should be erected between the cable trench and pedestrian/motor way to prevent accidents. The barriers shall be painted with yellow and black or red and white coloured cross stripes. Warning and caution boards should be consciously displayed. Red lights as warning signal should be placed along the trench during the nights.

The excavated material shall be properly stored to avoid obstruction to public and traffic movement.

The bottom of the excavated trench should be levelled flat and from any object which would damage the cable. Any gradient encountered shall be gradual.

20.10 LAYING OUT

The excavated cable trench shall be drained of all water and the bed surface shall be smooth, uniform and fairly hard before laying out the cable. The cable shall be rolled in the trench on cable rollers, spaced out of uniform intervals. The laying out process must be smooth and steady without subjecting the cable to abnormal tension. The cable on being laid out shall be smoothly and evenly transferred to the ground after  providing the  cushion.  The  cables  shall  never  be  dropped.  All snake bends shall be straightened. Suitable size cable stocking pulling eye  shall  be  used  for  pulling  the  cable.  While  pulling  the  cable  by winches   or   machines,   the   tension   loading   shall   be   by   tension indicator and shall not exceed the permissible value for the approved cable pulling tension calculation.

The cable end seal shall be checked after laying and if found damaged shall immediately be resealed. Sufficient number of heat shrinkable cable end sealing caps shall be stocked at site stores for testing and jointing work. The integrity of the outer sheath shall be checked after the cable is laid in position.

20.11	LAYING OF CABLES

The installation, testing and commissioning work for laying of cable in the entire route within the substation, through the outside cable laying corridor as per designated approved route shall mainly consist of:

    - Route survey for the entire route length under the scope of work. This is also to finalize drum wise cable length with their tolerances.

    - Clearances from relevant authorities for lying of cables.

    - Formation of buried cable trenches for cables as per specification including supply and installation of warning tape, protective tiles / brick layer of minimum class designation 50 (50kg./sq.cm.) cable protection covers for entire route, construction of jointing bays, back filling of trenches and restoration as per specification.

    - Road crossings shall be through HDPE pipe embedded in concrete duct for each cable and restoration as per specification. Rail and canal crossings shall be through direct drilling with steel drum.

    - Cable markers as per statutory requirements shall be provided all along the route at a maximum distance of 500 meters and other important locations. Also the location of underground cable shall be clearly indicated on the marker.

    - Supply and installation of straight through joints for complete route.

    - Design, supply and installation of suitable hangers and other necessary structures for running the cable at over head road bridge.

    - Supply and installation of all critical installation materials like trefoil clamps, neoprene cushions, support brackets etc. as required for complete route to avoid damages of the cable. Neoprene cushion shall be provided at road and rail bridge crossings to avoid damage of cable due to vibrations during movement of trains and vehicles.

i) Termination of cables, bonding of screen/sheath to the earth station through disconnecting type     link boxes and SVL (sheath voltage limiter) at cable conductor junction-point etc. Bidder shall adopt cable sheath bonding for route under scope as per detailed Engineering calculation in line with IEEE 575. Earthing stations/ Earthing pits, earthing materials and earthing conductors wherever applicable for complete route including outdoor equipment, structure, cable terminating structure and earth link box at the locations mentioned above shall be in contractors’ scope.

j) Design, fabrication, supply and erection of galvanized steel structures (including its civil foundation) for cable end terminations (with all necessary accessories) for cable sat cable–conductor junction point. At cable-conductor junction point terminal connectors offered by bidder shall be suitable to terminate with ACSR conductors.

k) For termination at GIS substation end the cable should be laid up to GIS module inside the GIS building. Necessary design construction of cable duct/ trench/ cellar etc. in the GIS Sub-Station including all supply is within the scope of this contract.

l) Design, supply and installation of LA sat cable–conductor junction point for both the circuits     including its mounting structure and Las & Isolator sat Sub-Station.

m) Termination, bonding, earthing etc. at GIS sub-station end is not within the scope of this work.

n) All EHV cable routes shall be provided with one linear heat sensing cable to detect any fire and provide alarm.

20.12	LAYING OVER PRE-CONSTRUCTED TRENCH

For laying of the cable on a pre-constructed trench below the road in any planned township area, Bridge, switchyards etc., cable shall have to be accommodated in the space allotted in the trench for laying the cables. Sufficient clamping arrangement shall be done for fixing the cable properly. Cables may be placed in trefoil arrangements as per allotted width of the trench. The clearances between the cable trays shall be minimum 330mm for cables up to 132kV and 400mm for cables  of  220kV  and  400kV.  For  66kV  cables,  maximum  two bends  are  allowed  in  20  mtr  span  and  for  132kV,  220kV  and 400kV  cables,  not  more  than  one  bend  shall  be  provided  in  20 mtr  span.  Any  damages  occurred  in  the  trench  during  lay  of  the cable shall have to be repaired properly. Wherever there is crossing with  any  utility  line,  the  utility  line  will  cross  the  cable  route/ jointing  bays  at  minimum  separation  distance  of  500mm  below cable route/ jointing bays.

20.13	CLAMPS

Clamps shall be pressure die cast aluminium (LM-6) or Nylon-6 or fiber glass and shall include neoprene rubber lining wherever the cable touches the clamps and below the clamp base and necessary fixing non magnetic nuts, bolts, washer etc. The thickness of neoprene rubber shall not be less than 10 mm inside around the inner surface of the trefoil clamp and minimum 20 mm thick below the base of trefoil clamp. The neoprene shall be tested as per ISIII49-1984. Clamps shall be provided at every one meter of cable runs. The contractor shall submit drawings of trefoil clamps and arrangements for Employer approval.

Self supported Aluminium Spring load clamp shall be provided for Cable termination structure at every 1 metre of cable run. The contractor shall submit the drawings of spring load clamp for employer’s approval.

20.14	CABLE HANDLING

The  inspection  of  cable  on  receipt,  handling  of  cables,  laying  out, flaking, cushioning with sand or sieved compacted soil, back-filling, reinstatement  of  road  surface,  providing  and  fixing  joint  markers, route  indicators,  precautions  of  joint  holes,  sump  holes  and  all necessary precautions that are required shall be carefully planned and in    general    conform    to    IS1255-    1983    or    its    equivalent.

CABLE JOINTING BAYS

Cable jointing bays shall be provided for single core EHV cables in a staggered manner along the cable route with adequate space for bonding of sheaths and link boxes as well as for testing. The jointing  bays  shall  have  adequate  number  of  cable  ducts  entry and exits including spare ducts with fire seals. The jointing bays shall have chequered covers of minimum 6mm thickness

  - DAMAGE TO PROPERTY

The contractor shall take all precautions while excavation of trench, trial pits etc., to protect the public and private properties and to avoid accidental damage. Any damages caused shall be immediately repaired and brought to the notice of the concerned and to the Employer.

    - The contractor shall bear all responsibilities and liabilities and shall bear all costs of the damages so caused by him or by his workman or agents.

    - At places where the cables cross private roads, gates of residential houses or buildings, the cables shall be laid in HDPE pipes of adequate strength using HDD technology.

20.15	CABLE ROUTE MARKERS / CABLE JOINT MARKERS

Permanent means of indicating the position of joints and cable route shall be fabricated supplied and erected as per drawings approved by AEGCL.

Cable markers as per statutory requirements shall be provided all along the route at a maximum distance of 30 meters and at all turning points and other important locations.

Markers provided shall be as per the field requirement, if the route passes through open fields, markers should be conspicuously visible above ground surface.

The marker should incorporate the relevant information, The name of the owner, voltage, circuit and distance of cable from the marker.

20.16	DEPTH OF LAYING OF CABLES

Depth of lay shall be normally at 1.5 m. below ground but variation of depth of lay to1 meter may be considered at the time of detailed engineering on the characteristics of the laying zone.

20.17	SAND BEDDING

The cable shall be completely surrounded by well-compacted cables and to such a thickness and of such size that the cable is protected against damage. The thickness of the cable sand should normally be a minimum of 10 cm in all directions from the cable surface.

20.18	THERMAL BACK FILL

Based on the evaluation of soil thermal resistivity along the cable route and after approval from the Employer the contractor shall design, specify, supply, lay and monitor the installation of thermal back fill surrounding the cables.

20.19	IMMEDIATE ENVELOPE TO CABLE

The option on the use of the material that immediately envelopes the cable viz., thermal back fill or sand or sieved native soil rests with the Employer. The contractor shall seek prior approval on the use of the envelop material from the Employer before execution of the works.

20.20	BACKFILLING

Normally back filling shall consist of the material earlier excavated. However, bigger stores or pieces of rock should be removed.

20.21	WARNING TAPE

A pre-warning, Red colour plastic/ PVC tape, 250 mm wide100 microns thick, shall be laid at approx. 0.4m above the cable specified depth, throughout the cable route. The tape shall carry the legend printed in black continuously as under

CAUTION: AEGCL ….. KV CABLES.

20.22	PREVENTION OF DAMAGE DUE TO SHARP EDGES

After the cables have been laid in the trench and until the cables are covered with protective covering, no sharp metal tool shall be used in the trench or placed in such a position that may fall into the trench.

Straight and curved rollers used shall have no sharp projecting parts liable to damage the cable.

While pulling through pipes and ducts, the cable shall be protected to avoid damage due to sharp edges. The cables shall never be bent, beyond the specified bending radius.

  - ROAD, RAIL & CANAL CROSSINGS

The road cutting, whether cement concrete asphalt or macadam road surface, rail crossing and canal crossing shall be taken after obtaining approval from the concerned authorities i.e. Railway authorities, irrigation deptt, civic authorities traffic police, telephone authorities etc. and work should be planned to be completed in the shortest possible time. Where necessary, the work shall be planned during night or light traffic periods. HDPE pipes shall be used for cable. HDPE pipes diameter should not be less than1.5 times the cable diameter.

20.24  TRENCHLESS DIGGING

It is envisaged that trenchless digging shall be used for crossing National highways, Rail line and canal and this shall be in the scope of bidder. Trenchless digging shall also be used where the concerned authorities do not permit open cut method and it is essentially required to carry out for installation of underground cables. The trenchless digging methods shall generally conform to ITU-T 1.38. The various methods of trenchless digging such as hand/ manual auguring (upto15m.) impact moulding (from 16m to about 40-50m.).HDD (above40-50m) shall be adopted based on the soil/ site conditions and the requirement and exact method for trenchless digging shall be finalized during detail engineering as per actual site/ soil condition. The equipment used for HDD shall be capable of drilling at least 100m at one go. The contractor shall propose the exact methods and procedures for implementation of trenchless digging at various crossings taking into consideration the following guidelines, for approval by the Employer.

- Guided boring/drilling technology is to be used.

- Radio or any detection system should be used for avoiding damage to existing underground utilities.

- The depth of boring should be such as to clear any underground utilities/obstacles. However in no case the depth of boring shall be less than 1.65m from the road surface.

- In horizontal and vertical boring, the system should be capable of going up to 10 meter below ground.

- The span of HDD will be decided in charge as per site requirements.

- Excavation and back filling of trial pits and verification of soil condition.

- Excavation of entry and Exit pits.

- Erection of drill machined. Drilling of pilot hole.

- Placement and driving hand augur.

- Placement and carrying out impact moling.

- Reaming and widening of bore holes in steps (if required).

- Pulling of product pipe.

20.25    FOOTPATH  CUTTING

The slabs, curb stones on the roads shall be removed and reinstated without damage. For laying of cables, the specified approved corridor shall be followed below footpath.

.

20.28	TOOLS AND PLANTS

The successful bidder shall have all necessary tools, plant and equipment to carry out the survey and cable installation work.

The bidders are instructed to give all the details of equipment at their disposal to carryout the work successfully and speedily.

20.29   BENDING RADIUS:

The minimum bending radius of XLPE insulated cables are as follows :

Cable Bending radius Single Core 25 X D

“D” means the overall diameter of the completed cable.

This bending radius is applicable for direct buried cable route and cable trench.

20.30     CABLE END TERMINATIONS & JOINTING

- The cable jointing accessories shall include the end terminating kits, straight through joints and also any special tools and tackles required for making these joints.

- The straight through joints shall be either Pre-molded Heat Shink type complete with all accessories.  The joint shall preferably be built up as per the construction of the main cable and shall have electrical and mechanical withstand capabilities same as or better than the main cable.  The joints shall be suitable for tropical climatic conditions.  All straight through joints and cable terminations shall have field proven experience of minimum five (5) years without any latent design defects.

- The outdoor end termination up to 245 KV XLPE Cable shall be Anti-fog, Pre-molded type Silicon Rubber stress cone. Torque controlled mechanical shear head bolted connector with polymeric composite housing (resin cast body with silicon shed housing), dry/fluid filled (silicon oil) type self-supporting with Plug-in /  Plug-out facilities.  The termination base plate and the cable's metallic sheath shall be electrically insulated from the self supporting structure by means of stand-off epoxy insulators designed to withstand both mechanical and electrical stresses in services. The Polymeric insulator in grey colour shall be used. In addition upon, arcing horn and shield ring shall have to be supplied as required for 245 & 420 KV XLPE cables. 10%etra silicon oil shall be supplied with termination if fluid filled is supplied.

- The outdoor end termination for 400kV shall be based on the Silicon / EPR-based stress relief cone with the epoxy housing and the oil-impregnated cylindrical capacitor cone (so called condenser cone type) to secure the uniform longitudinal voltage distribution all along the termination. Pre-molded type Silicon Rubber sleeve outdoor end termination for 400kV may be offered by the manufacturer if the same is available.

- The outdoor terminals should be suitable for heavily polluted atmospheric conditions with total creepage distance of 31 mm/ kV and protected creepage distance of not more than 50% of the total creepage distance. The cable end terminals for terminating the cables shall be fully compatible with the cables to be supplied.

- The Indoor Termination at GIS SF6 Housing shall be based on the Silicon Rubber based stress relief cone and the epoxy resin housing. There shall be mechanical devices to maintain the interface pressure. Stress relief cone and mechanical devices shall be designed to fit with controlled interference over the cable insulation and shall follow the cable's diameter variations still guaranteeing under any service condition a sufficient positive pressure to control the electric field concentration. There shall be epoxy insulating plate to isolate between cable sheath and GIS chamber. The SVLs (Sheath Voltage Limiter) shall be installed to protect epoxy insulating plate from switching impulse. Plug-in type leading conductors shall be supplied though at the time of detailed engineering confirmation shall be given for selection of plug-in type. Design and scope of delivery shall be fully complying with IEC-60859, IEC-62271-209 and possibly adjusted to various needs of project. The main insulation components shall be fully examined and tested in the factory.

- For jointing and terminations, one qualified Engineer and required trained EHV jointers with supporting staff should be deputed. The engineer and EHV jointers shall posses valid certificate from the manufacturer of the Accessories, for erection.

- The detailed description on jointing procedure shall be furnished during detailed engineering.

- The details of the performance of end terminations / straight through joints as offered with the period in service in reputed Indian Utility should be furnished for 145 KV & 245 KV and reputed  International/ Indian utility for 420 KV Cable accessories for evaluation of the techno-commercial offer.

- The accessories shall be Type Tested as per relevant IEC 60840 & Type test report shall have to be furnished for technical evaluation.

  - 20.31      WORKING PROCEDURE FOR TERMINATION

    - At cable terminating end sufficient length of spare cable shall be left in the ground and at cable tray also at GIS, for future needs.

    - The rise of the cable immediately from the ground shall be enclosed in PVC/ PE pipe of suitable diameter to protect against direct exposure to the sun.

    - The cable shall be properly fastened using non-metallic clamps.

    - Appropriate labels shall be fixed identifying the phase circuit, voltage and date of commissioning etc., on the cable supporting structure.

    - The sealing end shall be mounted on pedestal insulators to isolate them from their supporting steel work.

    - Protection from contact with the exposed metal work at the termination shall be provided by resin bonded glass fiber shroud.

    - Providing earth stations with all required materials, like leads, connectors etc. Earth pits shall conform to IS-3043:1987 (Code of practice for earthing).

  - 20.32     WORKING PROCEDURE FOR JOINTING

    - The cable jointing personnel and his crew shall have good experience and with HT license in the type of jointing and terminations that are used. The jointing works shall commence as soon as two or three lengths of cable have been laid. All care should be taken to protect the factory-plumbed caps/ seals on the cable ends and the cable end shall be sealed whenever the end is exposed for tests.

    - Jointing of cables in carriage ways, driveways under costly paving, under concrete or asphalt surfaces and in proximity to telephone cables and was mains should be avoided wherever possible.

    - Sufficient overlap of cables shall be allowed for making the joints.

    - The joint bay should be sufficient dimensions to allow the jointers to work with as much freedom of movement and comfort as possible. Sufficient space should be kept below the cable to be jointed. 3 ph link box for cross bonding to be placed inside the bay with provision for easy access for maintenance purpose.

#### The joints of different phases shall be staggered in the jointing bay.

    - Comprehensive jointing instructions should be obtained from the manufacture of jointing kits and meticulously followed.

    - The materials used in the joints like ferrules, screen/ sheath continuity bonds, lugs etc. shall be of good quality and conform to standards.

    - The jointing tools shall be appropriate and as per the requirement of jointing HVXLPE cables.

    - SUMPHOLES

When jointing cables in water logged ground or under unforeseen rainy conditions, a sumphole should be made at one end of the joint bay, in such a position so that the accumulated water can be pumped or drained out by buckets, without causing interference to the jointing operation.

    - TENTS/COVERS

An enclosure or suitable protection cover shall be used in all circumstances wherever jointing work is carried out in the open irrespective of the weather conditions. The joint shall be made in dust free, moisture free and clean atmosphere.

    - PRECAUTIONS BEFORE MAKING A JOINT

The cable end seals should not be opened until all necessary precautions have been taken to prevent circumstances arising out of rainy/ inclement weather conditions which might become uncontrollable.

If the cable end seals of cable ends are found to have suffered damage the cables should not be jointed, without tests and rectification.

    - MEASUREMENT OF INSULATION RESISTANCE

Before joining, the insulation resistance of both sections of cables shall be checked.

    - The identification of each phase shall be clearly and properly noted. The cables shall be jointed as per the approved design. Each cable shall have identification for phase at joint bays.

20.33 BONDING OF SCREEN/ SHEATH

The screens at both ends, shall be brought out and bonded to the earth station through disconnecting type link boxes or through SVL wherever applicable. On the basis of the length of the cable and current carrying capacity, the bonding maybe required as per IEEE 575 as follows:

1. Single End Bonding

2. Double End Bonding

3. Cross Bonding

4. Midpoint bonding

All accessories and consumables used in the termination should be of good quality and compatible with the cable. At the time of single end bonding parallel copper earth continuity conductor along the length of the cable shall have to be provided between the two ends of the cable. Bonding cable of 1.1KV copper XLPE insulated shall be provided for bonding of metallic sheath/ Screen.

The screens at both ends, shall be brought out and bonded to the earth station through disconnecting type link boxes or through SVL wherever applicable. On the basis of the length of the cable and rise of sheath Voltage the bonding maybe required as follows:

- Single End Bonding

- Double End Bonding

- Cross Bonding

- Mid point bonding

All accessories and consumables used in the termination should be of good quality and compatible with the cable. At the time of single end bonding parallel copper conductor along the length of the cable shall have to be provided between the two ends of the cable. Bonding cable of 6.6KV copper shall be provided for bonding of metallic sheath/ Screen.

20.34 CONNECTION OF RADIAL WATER BARRIER AND CABLE SCREEN

If the metallic radial water barrier is insulated from the metallic wire screen a connection suitable to carry the currents occurring during operation must be installed between metallic radial water barrier of the cable and metallic wire screen in joints and sealing ends.

20.35    STATUATORY APPROVAL OF WORKS

Contractor shall make an application on behalf of the owner for submission to the Electrical Inspectorate along with copies of required certificates complete in all respects and submit to the engineer-in-charge for onward transmission well ahead of time so that the actual commissioning of system/ equipment is not delayed for want of inspection by the Inspector. Contractor shall arrange the actual inspection of work by the Electrical Inspector. Necessary coordination and liaison work in this respect shall be the responsibility of the contractor.

The Inspection and acceptance of work as above shall not absolve the Contractor from any of his responsibilities under this contract.

Any other statutory approval of works required for the electrical installation (such as Factory Inspector, CCOE, etc.) is also included in contractor’s scope.

Supply & execution of job is subjected to regulations time to time framed by the AERC; approval Govt. Of Assam, and NOC from Assam Pollution Control Board. Contractor shall complete the entire job in compliance with the same.

20.36   INSPECTION, TESTING AND COMMISSIONING

- Inspection of Supplied materials and Site works time to time during execution:  Inspection of AEGCL and clearance from AEGCL will be in Contractor responsibility. Expenditure related to this inspection will be in contractor account.  Site inspection, testing and commissioning of electrical installation shall be carried out as per enclosed Specification and Inspection and Test Plans included or referred in this BID. All the equipment installed by the contractor shall be tested and commissioned, as required and no separate payments shall be made unless otherwise specified in the Schedule of Rates. Contractor shall carefully inspect all equipment and submit the manufacturer’s Certificate before installation. Any damage or defect noticed shall be brought to the notice of the engineer-in-charge at that time and same shall be rectified or replaced by CONTRACTOR on his OWN RISK AND COST within TIME FRAME. Complete testing of power transmission system would be carried out under the supervision of the Employer.

- Any work not conforming to the execution drawings, specifications or codes shall be rejected forthwith and the contractor shall carry out the rectification at his own cost.

- The contractor shall carry out all the tests as enumerated in the tender and technical specifications and technical documents which may be furnished to him during performance of the work.

- Before the electrical system is made live, the electrical contractor shall carry out suitable tests to establish to the satisfaction of the Employer that the installation of equipment, cabling/ wiring and connections have been correctly done and are in good working condition and that the system/ equipment will operate as intended.

- All tests shall be conducted in the presence of Employer/ Engineer-in-Charge or his authorized representative unless he waives this requirement in writing. Contractor shall arrange testing equipment, as required to carry out the tests. Test results shall be recorded on approved Performa and certified records of the tests shall be submitted to the Employer/ Engineer-in-Charge.

- Prior intimation to be given to the Employer before finalizing of date of scheduled inspection at least 15 days in advance.

- Clearance in favour of contractor for dispatch of equipment/material from respective works of manufacturer will be covered by the Employer after physical inspection and witnessing satisfactory routine and acceptance tests. Contractor will have to arrange physical inspection and witnessing of Routine and Acceptance Test of materials/equipments at respective manufacturer’s works by two engineer of the Employer and cost of such inspection shall have to be borne by contractor. Clearance for dispatch of equipments & materials from respective works of manufacturers will be conveyed by the Employer after verification and acceptance thereafter.

- After the completion of all tests and rectification of all defects pointed out during final inspection, plant start-up trials shall commence. During the start-up trials, contractor shall provide skilled/ unskilled personnel and supervision round the clock at his own cost. The engineer-in-charge/Employer will decide the number and the category of workmen and their duration. Any defects noticed during the start-up trials relating to the equipment supplied and work carried out by the contractor, shall be rectified by the contractor at his own cost.

- The Employer shall have the right to get the defects rectified at the risk and cost of the contractor if he fails to attend to the defects immediately as desired.

- Contractor shall also inform the Employer/ Engineer-in-charge, well in advance in case services of any OEM (Equipment manufacturer) are required and same shall be arranged by Contractor at the time of commissioning on his own cost.

- Contractor shall furnish site acceptance test (SAT) procedures from the equipment supplier and get it approved from the Employer/ Engineer-in-charge before carrying out the same at site.

- Contractor shall prepare detailed testing, pre-commissioning and commissioning procedures for the entire installation. These shall include Performa for defining activities and recording of test results.

- It is the responsibility of the contractor to coordinate and provide all necessary assistance to other contractors / agencies/ vendors involved in the complex for proper and timely execution of the works. Further contractor shall do all the liaisoning, documentation or other related formalities with respective authorities/agencies for successfully charging/commissioning of system.

- The following equipment/ items as included in Contractor’s scope of supply shall be tested and inspected by AEGCL or his authorized representative before dispatch at the manufacturer’s works. Test certificates duly signed by AEGCL or his authorized representative shall be submitted by the contractor as part of the final document:

a) EHV cable & optical fiber cables and Linear Heat sensing cable.

b) Jointing & termination kits for above items.

20.37 ENGINEERING DATA AND DRAWINGS

The Bidder shall necessarily submit all the drawings/ documents unless anything is waived. The Bidder shall submit 4(four) sets of drawings/ design documents/ data/ test reports as may be required for the approval of the Employer.

All drawings submitted by the Bidder including those submitted at the time of bid shall be in sufficient detail to indicate the type, size, arrangement, material description, Bill of Materials, weight of each component, break-up for packing and shipment, dimensions, internal and the external connections, fixing arrangement required and any other information specifically requested in the specifications.

All engineering data submitted by the Bidder after final process including review and approvalbytheEmployershallformpartoftheContractDocumentandtheentireworks performed under these specifications shall be performed in strict conformity, unless otherwise expressly requested by the Employer in Writing.

  - INSTRUCTION MANUAL

- The instruction Manuals shall contain full details of drawings of all equipment being supplied under this contract, their exploded diagrams with complete instructions for storage, handling, erection, commissioning, testing, operation, trouble shooting, servicing and overhauling procedures.

- If after the commissioning and initial operation, the instruction manuals require any modifications/ additions/ changes, the same shall be incorporated by the bidder in the final submission.

- The Bidder shall furnish to the Employer catalogues of spare parts.

  - QUALITY ASSURANCE PROGRAMME

- To ensure that the equipment and services under the scope of this Contract whether manufactured or performed within the Bidder’s Works or at his sub-bidder’s premises or at the Employer’s site or at any other place of work are in accordance with the specifications, the Bidder shall adopt suitable quality assurance programme to control such activities at all points necessary. Such programme shall be outlined by the Bidder and shall befinally accepted by the Employer after discussions before the award of Contract.

- Quality Assurance Documents

The Bidder shall be required to submit the following Quality Assurance Documents within three weeks before laying/ erection of the equipment.

  - All Non-Destructive Examination procedures, stress relief and weld repair procedure actually used during fabrication and reports including radiography interpretation reports.

  - Welder and welding operator qualification certificates.

  - Welder’s identification list, listing welder’s and welding operator’s qualification procedure and welding identification symbols.

  - Raw material test reports on components as specified by the specification and/or agreed to in the quality plan.

  - Stress relief time temperature charts/ oil impregnation time temperature charts.

  - Factory test results for testing required as per applicable codes/ mutually agreed quality plan/ standards referred in the technical specification.

  - The quality plan with verification of various customer inspection points (CIP) as mutually agreed and methods used to verify the inspection and testing points in the quality plan were performed satisfactorily.

  - EQUIPMENTS & STRUCTURES FOR CABLE TERMINATION

- The terminating structure being provided should be designed as per the requirement of the cable end sealing, porcelain bushing etc. The mounting structure shall be fixed on the cement concrete foundation, the design and drawings of which shall be submitted to Employer for review and acceptance during the course of detailed engineering.

After fixing the end termination, the cable shall be fixed to the support, with non- magnetic material clamps to the required height securely. The mounting structure includes the supports for cable end boxes, link boxes and any other structure required for the intent of the contract. All steel sections used shall be free from all imperfections, millscales, slag intrusions, laminations, fillings, rust etc. that may impair their strength, durability and appearance. All materials shall be of tested quality only unless otherwise permitted by the Employer.

- Suitable fencing should be provided at the cable terminating yard at cable conductor junction point. The fencing will consist of galvanized steel XPM structure over a brick wall of 2(two) feet meeting electrical requirement (IE). A suitable entry point (gate) has to be provided.

- Outdoor type lightning arresters for each cable of both the circuits are to be provided at cable-conductor junction point. The technical specification of lightning arresters is given separately in this volume.

- It is recognized that the Bidder may have standardized on the use of certain components, materials, processes or procedures different from those specified herein. Alternate proposals offering similar equipment based on the manufacturer’s standard practice will also be considered provided such proposals meet the specified designs, standard and performance requirements and are acceptable to the Employer. Unless brought out clearly, the Bidder shall be deemed to conform to this specification scrupulously. All deviations from the specification shall be clearly brought out in the respective schedule of deviations. Any discrepancy between the specification andthe catalogues or the bid, if not clearly brought out in the specific requisite schedule will not be considered as valid deviation.

- Equipment furnished shall be complete in every respect with all mountings, fittings, fixtures and standard accessories normally provided with such equipment and/or needed for erection, completion and safe operation of the equipment as required by applicable codes though they may not have been specifically detailed in the Technical Specifications unless included in the list of exclusions. Materials and components not specifically stated in the specification but which are necessary for commissioning and satisfactory operation of the work unless specifically excluded shall be deemed to be included in the scope of the specification and shall be supplied without any extra cost. All similar standard components/ parts of similar standard equipment provided shall be inter-changeable with one another.

- STEEL STRUCTURES (GANTRY, EQUIPMENTS ETC.):

- The contractor shall assume full responsibility for supply, fabrication and detailing, if required of the steel structures and for their satisfactory performance. All detail drawings for the structures shall be supplied to the successful bidder by the Employer/Engineer. However, the contractor shall have to submit the construction drawings to the Engineer/Employer solely prepared on the basis of these supplied drawings. Equipment Structure drawings, supplied by the employer, shall have to be modified to suit to the approved GA drawings of the equipment and electrical layout drg. And to be submitted to Engineer for approval. Employer/ Engineer shall have the right to instruct the contractor to make any changes in details necessary to make the construction conform to the requirement of the Contract Document.

- The contractor shall supply all materials, deliver the same to site, and provide all labour, erection plant and equipment, fixtures, fitting and all temporary and permanent works necessary for satisfactory completion of the job in all respects.

- No omissions or ambiguities on the drawings or in specifications will relieve the contractor from furnishing best quality of materials and workmanship. Should any inaccuracies be found, the contractor shall promptly notify the Employer/Engineer without carrying out the job and no further work shall be done before these discrepancies are corrected. Continuation of further work shall be done only after such discrepancies are rectified at contractor's risk and responsibility.

- MATERIALS: The materials shall conform to the following requirements:

All Structural Steel Materials to be used in construction within the purview of the specification shall comply with :IS:2062 –Structural Steel (Grade-A) (fusion welding quality) and manufactured by Prime Rollers e.g. SAIL/ TISCO/ IISCO/ RINL. In case of MS sections not manufactured by prime rollers or such sections are not available with prime rollers the same is to be procured from approved conversion agents of prime manufacturer(s).In such case, prior approval of the Engineeris to be obtained by the contractor.

Successful bidder on receipt of structural drawing from department shall submit within 15 days, a detailed raw material procurement plan indicating MS sectionwise producers name to the Engineer for approval. On according approval in this aspect, work for fabrication protos shall be taken up in hands.

Entire fabrication job of MS structural shall not be entrusted to more than two sub- vendors. Further, a list of bonafide fabricators, not exceeding 6 (six) shall be furnished to the Engineer for according approval within 15(fifteen) days from the date of handing over of drawings.

All electrodes to be used under the contract shall comply with any of the following Indian Standard Specifications as may be applicable.

- IS:814: Covered electrodes for metal arc welding of Structural Steel.

- IS:815: Classification and coding of covered electrodes for metal arc welding of mild steel and low alloy high tensile steel.

- IS:144: Covered electrodes for the metal arc welding of high tensile structural steel.

  - All bolts and nuts shall be of grade 5.6HRH and shall conform to the requirements of IS:6639 and IS:1367 and galvanizing quality shall be as per IS:1367.  All bolts and nuts shall be of minimum diameter of 16mm unless otherwise stated. All mildsteel for bolts and nuts when tested in accordance with the following Indian Standard specification shall have a tensile strength of not less than 44Kg/Sq.mm. and a minimum elongation of 23 percent on a gauge length of 5.6A, where `A' is the cross sectional area of the test specimen-

- IS:1367: Technical supply conditions for threaded fasteners.

- IS:1608: Method for tensile testing of steel products other than sheet, strip, wire and tube.

Washers shall be made of steel conforming to IS:226, IS:961 as may be applicable under the provisions of the contract and shall be electrogalvanized.

7 FASTNERS & CONNECTIONS:

- BOLTS: All connections shall be bolted with 16mm bolts.

- SPLICES: Splicing shall be avoided unless the length of a member exceeds 6.0 m or so. The member of splices shall be limited to a practical minimum. No credit shall be allowed for bearing on a butting areas. Lap joints in leg members shall be preferred to butt joints.

- STEP BOLTS: Step bolts shall be of 16mm diameter and shall have round or hexagonal head. Each step bolt shall be provided with two hexagonal nuts. The minimum bolt length and length of unthreaded portion shall be 180 and 125mm respectively. Step bolts shall not be used as connection bolts. The step bolts shall be spaced alternately on the inner gaugelineoneachfaceoftheangleabout40cmcenters.Theyshallbefurnished for one leg of each steel structure column from its base elevation.

- U – BOLTS: U-Bolts shall be suitable furnished or steel structures to suspend or terminate insulator strings or ground wire assemblies. Size of U-bolt shall withstand all loads acting on it.

- BILL OF MATERIAL: Bill of material shall give the size, length and weight of each member and the total weights of steel structures. It shall also include the number of bolts, nuts and washers per structure.

  - MATERIAL/ WORKMANSHIP

Where the specification does not contain references to workmanship, equipment, materials and components of the covered equipment, it is essential that the same must be new of highest grade of the best quality of their kind conforming to best engineering practice and suitable for the purpose for which they are intended.

In case where the equipment, materials or components are indicated in the specification as “similar” to any special standard, the Employer shall decide upon the question of similarity. When required by the specification or when required by the Employer the Bidder shall submit, for approval, all the information concerning the materials or components to be used in manufacture, Machinery, equipment, materials and components supplied, installed or used without such approval shall run the risk of subsequent rejection, it being understood that the cost as well as the time delay associated with the rejection shall be borne by the Bidder.

The design of the Works shall be such that installation, future expansions, replacements and general maintenance may be undertaken with a minimum of time and expenses. Each component shall be designed to be consistent with its duty and suitable factors of safety, subject to mutual agreements. All joints and fastenings shall be devised, constructed and documented so that the component parts shall be accurately positioned and restrained to fulfill their required function. In general, screw threads shall be standard metric threads. The use of other thread forms will only be permitted when prior approval has been obtained from the Employer.

Whenever possible, all similar part of the Works shall be made to gauge and shall also be made interchangeable with similar parts. All spare parts shall also be interchangeable and shall be made of the same materials and workmanship as the corresponding parts of the Equipment supplied under the Specification. Where feasible, common component units shall be employed in different pieces of equipment in order to minimize spare parts stocking requirements. All equipment of the same type and rating shall be physically and electrically interchangeable.

All materials and equipment shall be installed in strict accordance with the manufacturer’s recommendation(s). Only first-class work in accordance with the best modern practices will be accepted. Installation shall be considered as being the erection of equipment at its permanent location. This, unless otherwise specified, shall include unpacking, cleaning and lifting into position, grouting, leveling, aligning, coupling of or bolting down to previously installed equipment bases/ foundations, performing the alignment check and final adjustment prior to initial operation, testing and commissioning in accordance with the manufacturer’s tolerances, instructions and the Specification.

Provision for Exposure to Hot and Humid climate: Outdoor equipment supplied under the specification shall be suitable for service and storage under tropical conditions of high temperature, high humidity, heavy rainfall and environment favourable to the growth of fungi and mildew.

  - PACKAGING & PROTECTION

- All the equipment shall be suitably protected, coated, covered or boxed and crated to prevent damage or deterioration during transit, handling and storage at Site till the time of erection. On request of the Employer, the Bidder shall also submit packing details/ associated drawing for any equipment/ material at a later date, in case the need arises. While packing all the materials, the limitation from the point of view of availability of Railway wagon sizes in India should be taken into account. The Bidder shall be responsible for any loss or damage during transportation, handling and storage due to improper packing. Any demurrage, wharf age and other such charges claimed by the transporters, railway etc. shall be to the account of the Bidder. Employer takes no responsibility of the availability of the wagons.

- All coated surfaces shall be protected against abrasion, impact, discoloration and any other damages. All exposed threaded portions shall be suitably protected with either a metallic or a non-metallic protecting device. All ends of all valves and piping and conduit equipment connections shall be properly sealed with suitable devices to protect them from damaged. The parts which are likely to get rusted, due to exposure to weather should also be properly treated and protected in a suitable manner.

  - FINISING OF METAL SURFACES

- All metal surfaces shall be subjected to treatment for anti-corrosion protection. All ferrous surfaces for external use unless otherwise stated elsewhere in the specification or specifically agreed shall be hot-dip galvanized after fabrication. High tensile steel nuts and bolts and spring washers shall be electro galvanized to service condition. All steel conductors including those used for earthing/grounding (above ground level) shall also be galvanized accordingtoIS:2629.

- HOT DIP GALVANISHING

The minimum weight of the zinc coating shall be 900gm/sq.m and minimum thickness of coating shall be 130 microns for outdoor and minimum thickness of coating shall be 85 microns for indoor for all items thicker than 6mm. For items lower than 6mm thickness requirement of coating thickness shall be as per relevant ASTM. For surface, which shall be embedded in concrete the zinc coating shall be 610gm/sqm minimum.

- The galvanized surfaces shall consist of a continuous and uniform thick coating of zinc firmly adhering to the surface of steel. The finished surface shall be clean and smooth and shall be free from defects like discoloured patches bare spots, unevenness of coating, spelter which is loosely attached to the steel globules, spiky deposits, blistered surface, flaking or peeling off etc. The presence of any of these defects noticed on visual or microscopic inspection shall render the material liable to rejection.

After galvanizing no drilling or welding shall be performed on the galvanized parts of the equipment excepting that nuts may be threaded after galvanizing. Sodium dichromate treatment shall be provided to avoid formation of white rust after hot dip galvanization.

The galvanized steel shall be subjected to six one minute dips in copper sulphate solution as per IS-2633.

Sharp edges with radii less than 2.5mm shall be able to withstand four immersions of the Standard Preece test. All other coatings shall withstand six immersions. The following galvanizing tests should essentially be performed as per relevant Indian Standards

- Coating thickness

- Uniformity of zinc

- Adhesion test

- Mass of zinc coating

Galvanized material must be transported properly to ensure that galvanized surfaces are not damaged during transit. Application of zinc rich paint at site shall not be allowed.

- PAINTING

- All sheet steel work shall be degreased, pickled, phosphate in accordance with the IS-6005 “Code of practice for phosphating iron and sheet”. All surfaces which will not be easily accessible after shop assembly shall be forehand be treated and protected for the life of the equipment.

- The surfaces, which are to be finished painted after installation or require corrosion protection until installation shall be shop painted with at least two coats of primer. Oil, grease, dirt and swaf shall be thoroughly removed by emulsion cleaning. Rust and scale shall be removed by pickling with dilute acid followed by washing with running water, rinsing with slightly alkaline hot water and drying.

- After phosphating, thorough rinsing shall be carried out with clean water followed by final rinsing with dilute dichromate solution and oven drying. The phosphate coating shall be sealed with application of two coats of ready mixed, stoving type zinc chromate primer. The first coat may be “flash dried” while the second coat shall be stoved.

- After application of the primer, two coats of finishing synthetic enamel paint shall be applied each coat followed by stoving. The second finishing coat shall be applied after inspection of first coat of painting.

- The exterior color of the paint shall be as per shade no: 697 of IS-5 and inside shall be glossy white for all equipment, marshalling boxes, junction boxes, control cabinets, panels etc. unless specifically mentioned under respective sections of the equipments. Each coat of primer and finishing paint shall be slightly different shade to enable inspection of the painting. A small quantity of finishing paint shall be supplied for minor touching up required at site after installation of the equipments.

- In case the Bidder proposes of follow his own standard surface finish and protection procedures or any other established painting procedures like electrostatic painting etc. the procedure shall be submitted along with the Bids of Employer’s review and approval.

  - HANDLING, STORING AND INSTALLATION

- In accordance with the specific installation instructions as shown on manufacturer’s drawings or as directed by the Employer or his representative, the Bidder shall unload, store, erect, install, wire, test and place in to commercial use all the equipment included in the contract. Equipment shall be installed in a neat, workman like manner so that it is level, plumb, square and properly aligned and oriented. Commercial use of switchyard equipment means completion of all site tests specified and energization at rated voltage.

- Bidder may engage manufacturer’s Engineers to supervise the unloading, transportation to site, storing, testing and commissioning of the various equipment being procured by them separately. Bidder shall unload, transport, store, erect, test and commission the equipment as per instructions of the manufacturer’s supervisory Engineer(s) and shall extend full cooperation to them.

- In case of any doubt/ misunderstanding as to the correct interpretation of manufacturer’s drawings or instruction, necessary clarifications shall be obtained from the Employer. Bidder shall be held responsible for any damage to the equipment consequent to not following manufacturer’s drawings / instructions correctly. Where material/ equipment is unloaded by Employer before the Bidder arrives at site or even when he is at site. Employer by right can hand over the same to Bidder and there upon it will be the responsibility of Bidder to store the material in an orderly and proper manner.

- The Bidder shall be responsible for making suitable indoor storage facilities to store all equipment, which require indoor storage.

- The words ‘erection’ and ‘installation’ used in the specification are synonymous.

- Exposed live parts shall be placed high enough above ground to meet the requirements of electrical and other statutory safety codes.

- The design and workmanship shall be in accordance with the best engineering practices to ensure satisfactory performance throughout the service life. If at any stage during the execution of the Contract, it is observed that the erected equipment(s) do not meet the above minimum clearances as given in clause 4.7.1 the Bidder shall immediately proceed to correct the discrepancy at his risks.

  - QUALITY CONTROL:

- The contractor shall establish and maintain quality control procedures for different items of work and materials to ensure that all work is performed in accordance with the specifications and best modern practice.

- In addition to the Contractor's quality control procedures, materials and workmanship at all times shall be subjected to inspection by the Engineer. As far as possible all inspection by the Engineer or Engineer's representative shall be made at the Contractor's fabrication shop whether located at site or elsewhere. The contractor shall cooperate with the Engineer in permitting access for inspection to all places where work is being done and in providing free of cost of all necessary help in respect of tools and plants, instrument, labour and material required to carry out the inspection. Materials or workmanship not in reasonable conformance with the provisions of this specification may be rejected at any time during the progress of the work.

- The quality control procedure shall cover but not be limited to the following items of work :

- Steel: Quality, manufacturer's test certificates, test reports including procurement in-voice of representative  samples of materials from unidentified stocks if permitted to be used.

- Bolts, nuts & Washers: Manufacturer's certificate, dimension check, material testing

- Electrodes: Manufacturer's certificate, thickness and quality of flux coating.

- Welds: Inspection, X-ray, ultrasonic test, magnetic particle tests as required

- Paints: Manufacturer's certificate, physical inspection reports.

- Galvanizing: Tests in accordance with IS:2633 – Method of testing uniformity of coating on zinc coated articles and IS:2629 Recommended practice for hot - dip galvanizing of iron and steel.  Raw zinc & samples collected from bath shall be tested at third party laboratory as per direction of the Engineer.

- The contractor shall submit a detailed material inspection plan on the basis of various IS codes & standard practices in respect of structural fabrication, galvanization, bolts, nuts, anchor bolts etc. much prior to commencement of the job.

20.44       FABRICATION WORKMANSHIP:

- All workmanship shall be equal to the best practice in modern structural shop and shall conform to the provisions of IS:800/ IS:802.

- Rolled materials before being laid off or worked, must be clean free from sharp kinks, bends, or twists and straight within the tolerances allowed by IS:1852. If straightening is necessary it may be done by mechanical means or by the application of a limited amount of localised heat not exceeding 600oC.

- Cutting shall be effected by shearing, cropping or sawing. Use of mechanically controlled Gas Cutting Torch may be permitted for mild steel provided special care is taken to leave sufficient metal to be removed by machining, so that all metal that has been hardened by flame is removed. To determine the effective size of members cut by gas, 3mm shall be deducted from each cut edge.

- The erection clearance for cleated ends of members connecting steel to steel shall preferably be not greater than 2mm at each end. The erection clearance at ends of beams without cleats shall not be more than 3mm at each end, but where for practical reasons greater clearance is necessary, suitably designed clearance shall be provided.

- All members shall consist of rolled steel sections.

- Holes for bolts shall not be more than 1.5mm larger than the diameter of the bolt passing through them unless otherwise stated.

- All members shall be cut to jig and all hole shall be punched and drilled to jig. All parts shall be carefully cut and holes accurately located after the members are assembled and tightly clamped or bolted together.

- Drifting or rimming of holes shall not be allowed. Holes for bolts shall not be formed by gas cutting process.

- Punching of holes will not be permitted for M.S. members upto 8mm thick and in no case shall a hole be punched where the thickness of the material exceed the diameter of the punched hole.

- Minimum bolt spacing and distances from edges of members shall in accordance withthe provisions in the relevant Indian Standard Specification.

- Built members shall, when finished, be true and free from all kinds of twists and open joints and the material shall not be defective or strained in any way.

- All bolts shall be galvanized including the threaded portion except the foundation bolts for which galvanizing work shall be done for a length of 100mm (min) to 175mm (max) measured from the tip of the treaded portion. The threads of all bolts shall be cleared of smelter by spinning or brushing. A die shall not be used for cleaning the threads unless specially approved by the Engineer. All nuts shall be galvanized with the exception of the threads which shall be oiled. In case of foundation bolts the same shall be galvanized excepting the length of embedment.

- When in position all bolts shall project through the corresponding nuts but not exceeding 10 mm. The nuts of all bolts attaching insulator sets and earth conductor clamps to the structure shall be carefully positioned as directed by the Engineer.

- Bolts and nuts shall be placed in such a way so that they are accessible by means of an ordinary spanner.

- Foundation bolts shall be fitted with washer plates or anchor angles and flats, nuts etc. and shall be manufactured from mild or special steel.

- Washers shall be tapered or otherwise suitably shaped, where necessary to give the heads and nuts of bolts a satisfactory bearing. The threaded portion of each bolt shall project out through the nut at least by 3mm. In all cases the bolt shall be provided with a washer of sufficient thickness under the nut. In addition to the normal washer, one spring washer or lock nut shall be provided for each bolt for connections subjected to vibrating forces or otherwise as may be specified in the drawings.

- The thickness of spring washer shall be 3.5 mm for bolt diameter 16 mm and 4 mm for bolt diameter 20 mm.

20.45 CLEANING & GALVANIZING:

20.45.1 CLEANING:

After fabrication has been completed and accepted, all materials shall be cleared off rust, loose scale, dirt, oil grease and other foreign substances.

20.45.2 GALVANIZING:

All materials shall be hot-dip galvanized after fabrication and cleaning. Re tapping of nuts after galvanizing is not permitted.

Galvanizing for structural mild steel products shall meet the requirements of IS:4759. All holes in materials shall be free of excess spelter after galvanizing.

Galvanizing for fasteners shall meet the requirements of IS:1367. The spring washers shall be electrogalvanized as per IS:1573.

Finished materials shall be dipped in to the solution of dichromate after galvanizing for white rust protection during transportation.

All galvanizing shall be uniform and of standard quality. Quantity of zinc shall meet the requirement of IS:209.

Mass of Zinc Coating:

The mass of zinc coating for different class of materials, as given in Table below, shall be followed:

MASS OF ZINC COATING

| Sl. No. | Product | Electro meter reading (micron) | Minimum value of average mass of coating |
| --- | --- | --- | --- |
| i) | Casting - gray iron, malleable iron |  | 610 (gm/m2) |
| ii) | Fabricated steel articles : |  |  |
| a) | 5 mm thick and over | 86 | 610 |
| b) | Under 5 mm, but not less than 2 mm | 65 | 460 |
| c) | Under 2 mm, but not less than 1.2mm | 48 | 340 |
| iii) | Threaded work other than tubes and tube fittings : |  |  |
| a) | 10 mm dia and over | 43 | 300 |
| b) | Under 10 mm dia | 39 | 270 |
| iv) | All Outdoor structures | 130 | 900 |

Technical Specification of Distributed Temperature Monitoring System (DTS)

The bidder shall include and provide separate “Distributed Temperature Monitoring System (DTS)” for entire route for EHV Cables complete in all respects along with terminal coupling equipment, workstation and required hardware and software for real time monitoring of conductor temperature profile (with ambient temperature compensation) and to provide dynamic power load predictions of the cable based on relevant IEC standards. The offered system should be able to provide maximum possible transmission capacity of the cable for each circuit. The distributed temperature monitoring system shall be optical fiber based, must be of proven technology and should be in operation for similar use along with EHV cables as per latest practices. The DTS shall be inherently resistant to taking a given reading and giving a false alarm due to the requirement for multiple physical effects (Viz. temperature/hot spot, strain, arc flash, optical Loss, Fiber Break, Conductor break, etc.) to simultaneously occur at the same location to signify an event and trigger an alarm with Geo-tags. The DTS system can be calibrated to run very quick (a few seconds), lower accuracy (±1°C) scans of the fibre for temperature changes or to take a slower (half a minute) more detailed scan for maximum accuracy (±0.25°C) of temperature to sense even the smallest changes. The DTS shall be passive, no electricity is required in the field. Also, no maintenance or calibration shall be required after commissioning. The self-diagnostics of DTS shall monitor the unit’s condition and maintain optimum performance. The DTS shall not be affected by electromagnetic fields (EMF), lightning or weather events. The DTS unit can be attached as a loop to both channels on independent fibres and in the event of a cut will report the damage, but continue to monitor the fiber on both sides up to the cut. The “terminal coupling equipment” and “workstation” shall preferably be microprocessor based with HMI, for displaying temperature along the length of the cable system. System shall provide potential free output contact for signaling to SCADA. The bidder shall provide brochures and catalogues for offered distributed temperature monitoring system along with the bid. Optical fiber cables along with all joining accessories etc. required for DTS shall also be included in the scope of bidder. Optical fiber cable associated with DTS shall be laid in the same EHV cable trench/raceway.

General Technical Specifications of DTS

(All blank parameters shall be filled-up by Vendor/EPC)

| Sl. No. | Parameter | Description |
| --- | --- | --- |
| 1. | Sensing Element | Fibre Optic Sensing Cable |
| 2. | Number of channels (Dual Channel) |  |
| 3. | Interrogator operating Temperature | 0-50°C |
| 4. | operating Humidity (max) | As per GTR |
| 5. | Dimensions (Rack mounted) |  |
| 6. | Weight (Kg) |  |
| 7. | Power Supply (V) |  |
| 8. | Power consumption (W) |  |
| 9. | Sensing Range (DTS) (km) Loop Per channel |  |
| 10. | Spatial Resolution (250 or 500mm) |  |
| 11. | Frequency Response | 1Hz-120kHz (Range Dependant) |
| 12. | Temperature sensing range (cable) | -5°C to 700°C |
| 13. | Accuracy |  |
| 14. | Resolution |  |
| 15. | Scan Time |  |
| 16. | Light Source | Laser (Infra-red) Class 1M |
| 17. | Laser Wave Length | As per IEC |
| 18. | Laser Stability | As per IEC |
| 19. | Acquisition rate |  |
| 20. | Processor Acquisition Rate | 64Bit (Ultra high speed) |
| 21. | Operating System |  |
| 22. | Output | Modbus, Ethernet, TCP/IP (Standard), Relay, USB, SCADA, IEC 61850 or equivalent |
| 23. | Remote Interfacing | Ethernet and 4G/5G enabled |
| 24. | Processer architecture | Field programmable gate array (FPGA) |
| 25. | Data Storage (Removable) | 2x 2TB HDD (removable) [Minimum] |
| 26. | Data Storage (Internal) | 128GB Solid State Drive [Minimum] |
| 27. | Dynamic Range |  |
| 28. | Standard | IEC 61757-2-2: 2016 and other relevant IEC |
| 29. | Any other parameters to be filled by Manufacturer |  |
| 30. | Firmware and software details (Latest Version) |  |
| 31. | Warranty Period |  |
| 32. | License validity period (if any) |  |
| 33. | Measurement reach (km) |  |

Table 2: CHAPTER  26: SPECIFICATION FOR DESIGN AND FABRICATION OF SUB STATION STEEL STRUCTURES

STRAIGHTENING  AFTER  GALVANIZING:

All plates and shapes which have been warped by the galvanizing process shall be straightened by being rerolled or pressed. The materials shall not be hammered or otherwise straightened in a manner that will injure the protective coating. If, in the opinion of Employer/ Engineer the material has been forcibly bent or warped in the process of galvanizing of fabrication, such defects shall be cause for rejection.

REPAIR OF GALVANIZING:

Materials on which galvanizing has been damaged shall be acid stripped and re-galvanized, unless, in the opinion of Engineer, the  damage is local and can be repaired by zinc spraying or by applying a coating of galvanizing repair compound. Where re-galvanizing is required, any member which become damaged after having been dipped twice shall be rejected.

SHOP ASSEMBLY:

One of each type of steel structures shall be assembled in the shop to such an extent as to ensure proper field erection in order to facilitate inspection by the Engineer.

SHOP TEST:

The following shop tests shall be performed with relevant provisions of I.S. Codes :

- General Inspection

- Material test.

- Assembly test.

- Galvanizing test.

The contractor shall furnish four certified copies of reports of all tests to the Engineer.

  - DESIGN OF FOUNDATIONS:

    - STEEL STRUCTURE FOUNDATIONS:

The foundations shall be designed such that the upper structure shall be securely supported. Any unequal displacement that may cause harmful effect to the upper structures shall not be allowed. The safety factors for strength and stability of the foundations shall be as per relevant code.

The overload factor shall be taken as 1.1 for designing foundations of all gantry and equipment. The loads, shear and moment values shall be multiplied with this overload factor, so as to obtain the design values

20.49   WEIGHT OF SUB-STATION STRUCTURES:

Self-weight of line tower, A-frame and equipment structures for different gantry and equipment structures shall be provided at the time of detail engineering.

20.50  Technical Specification for Underground Fibre Optic Cable

This section describes the functional requirements, major technical parameters and Type testing, Factory Acceptance Testing & Site Acceptance Testing requirements for underground fibre optic cables and HDPE pipes. Marking, packaging, transportation & installation requirements have also been described. The payment will be made for the executed route length only. However, specified service loops and lengths for wastage, installation/working for FO cable & HDPE ducts shall be considered as required by the bidder for which no additional payment will be made.

20.50.1 General

The underground fibre optic cable shall be armoured and shall be suitable for direct burial as well as for underground installation in pipes. The cable should be of low weight, small volume and high flexibility. The mechanical design and construction of each unit shall be inherently robust and rigid under all condition of operation, adjustment, replacement, storage and transport. The fibre optic cable shall be a UV resistant, rodent proof. The underground fibre optic cable (UGFO) shall be offered from a manufacturer who has been manufacturing UGFO for the last five (5) years and UGFO manufactured & supplied by such manufacturer shall have been in satisfactory operation.

20.50.2 	Applicable Standards

The cable shall conform to the standards named below and the technical specifications described in the following sections.

i). 	ITU-T Recommendations G.652

ii).	Electronic Industries Association, EIA/TIA 455-78A, 455-3A/33/41/25A / 81A / 82B, 455-62A, 455-164A/167A/174, 455-168A/169A/170/175A, 455-176, 455-59, EIA/TIA 598, EIA 455- 104.

iii)	International Electro technical Commission standards, IEC60304, IEC60794-1-2, IEC60811-5-

iv)	 Bellcore GR-20

v)	Indian Railways standard specification no IRS:TC55(Oct 96) (including all amendments)

vi)	ASTM:A167-92,ASTM:751-92b,ASTM:A751-92,ASTM:A370-82,ASTM:D2581-

91,ASTM:D2287-81, ASTM:D 638 for FRP, ASTM :D 217,556, 93-IP-34 for Jelly, ASTM:D

570,211 for PBTP, ASTM:D1505for Poly Carbonate, ASTM:D1633,150 for HDPE.

20.50.3 	Fibre Type(s) and Counts

The Cable shall consist of 24 fibres Dual-Window Single mode (DWSM), G.652 optical fibres and shall meet the requirements stipulated in Table 1

DWSM Optical Fibre Characteristics(Table-1)

| Fibre Description: | Dual-Window Single-Mode |
| --- | --- |
| Mode Field Diameter: | 8.6 to 9.5 µm (± 0.6 µm) |
| Cladding Diameter: | 125.0 µm +/- 1 µm |
| Mode Field concentricity error | ≤0.6% |
| Cladding non-circulatory | ≤ 1% |
| Cable Cut-off Wavelength λcc | ≤ 1260 nm |
| 1550 nm loss performance | As per G .652 |
| Proof Test Level | ≥ 0.69 Gpa |
| Attenuation Coefficient: | @ 1310 nm ≤ 0.35 dB/km @ 1550 nm ≤ 0.21 dB/km |
| Chromatic Dispersion; Maximum: Zero Dispersion Wavelength: Zero Dispersion Slope: | 18 ps/(nm x km) @ 1550 nm 3.5 ps/(nm x km) 1288-1339 nm 5.3 ps/(nm x km) 1271-1360 nm 1300 to 1324 nm 0.092 ps/(nm2xkm) maximum |
| Polarization mode dispersion Coefficient | ≤0.2 ps/km^1/2 |
| Temperature Dependence: | Induced attenuation ≤ 0.05 dB (-600C - + 850C) |
| Bend Performance: | @ 1310 nm (75±2 mm dia Mandrel), 100 turns; Attenuation Rise ≤0.05 dB @ 1550 nm (30±1 mm radius Mandrel) 100 turns; Attenuation Rise ≤ 0.05 dB @ 1550 nm (32±0.5 mm dia Mandrel, 1 turn; Attenuation Rise ≤ 0.50 dB |

20.50.4	General Cable Construction

Consist of a central fibre optic unit protected by one or more layers of helically wound anti-hygroscopic tape or yarn. The central fibre optic unit shall be designed to house and protect the fibres from damage due to forces such as crushing, bending, twisting, tensile stress and moisture, wide temperature variations, hydrogen evolution etc. The fibre optic unit shall be of loose tube construction. The inner polyethylene jacket and outer sheath jackets shall be free from pinholes, joints, splits or any other defects. All fibre optic cable shall have a minimum service life span of 25 years. The cable construction and mechanical parameters for the Armoured OFC shall be as specified in the Table 2 below.

| Table 2 Armoured Cable Construction and Mechanical Parameters |  |  |
| --- | --- | --- |
| Parameter | Units | Description |
| No of fibres in the cable |  | 24 |
| Type of fibres in the cable |  | G.652 |
| No. of loose tubes |  | Minimum 2 |
| Cable design life |  | More than 25 years |

20.50.5 Colour Coding & Fibre Identification

Individual optical fibres within a fibre unit, and fibre units shall be identifiable in accordance with EIA/TIA 598 or IEC 60304 or Bellcore GR-20 colour-coding scheme. The colour coding system shall be discernible throughout the design life of the cable. Colouring utilized for colour coding optical fibres shall be integrated into the fibre coating and shall be homogenous. The colour shall not bleed from one fibre to another and shall not fade during fibre preparation for termination or splicing. Each cable shall have traceability of each fibre back to the original fibre manufacturer’s fibre number and parameters of the fibre. If more than the specified number of fibres are included in any cable, the spare fibres shall be tested by the cable manufacturer and any defective fibre shall be suitably bundled, tagged, and identified at the factory. The colouring scheme shall be submitted along with the cable DRS/drawing for Employer’s approval.

20.50.6 Strength Members

The armoured optical fibre cable shall have solid non-metallic strength member(s)/ Solid metallic member(s) or the combination of both. The metallic strength member shall be of high grade steel wire, music spring quality as per ASTM-A228/A228M-93 and shall have suitable chemical coating for proper adhesion with sheath material. The central fibre optic unit should include a central strength member of non-metallic Fibre Reinforced Plastic (FRP) only. Peripheral strength members and aramid yarns are also acceptable. The central FRP strength member may be of slotted type with SZ lay (reverse oscillation lay) of fibre units or it may be cylindrical type with helical or SZ lay of fibre units. The construction of the central strength member shall be such as to meet the mechanical strength requirements specified in this specification.

20.50.7 Filling Compound

The interstices of the central fibre optic unit and cable shall be filled with a suitable compound to prohibit any moisture ingress or any longitudinal water migration within the fibre optic unit or along the fibre optic cable. The water tightness of the cable shall meet or exceed the test performance criteria as per IEC60794-1-2-F5. The filling compound used shall be a non-toxic homogenous waterproofing compound that is free of dirt and foreign matter, anti-hygroscopic, electrically nonconductive and non-nutritive to fungus. The compound shall also be fully compatible with all cable components it may come in contact with and shall inhibit the generation of hydrogen within the cable. The filling compound shall remain stable for ambient temperature up to +70°C and shall not drip, flow or leak with age or at change of temperature. Reference method to measure drip point shall be as per IEC 60811-5-1 and drip point shall not be less than 70°C.

20.50.8 The Sheath / Inner jacket

The Sheath shall be made of High Density Polyethylene-HDPE (Red /Black) and shall be smooth, concentric, and free from holes, splits, blisters and other surface flaws. The sheath shall be extruded directly over the central fibre optic unit and shall also be non-hygroscopic. The cable sheath design shall permit easy removal without damage to the optical fibres or fibre units. The sheath shall be made from good quality of weather resistant polyethylene compound HDPE and thickness shall be > 1.5mm including the strength member if used in the sheath.

20.50.9 Armouring of cable

Over the inner PE sheath armouring and outer sheath shall be provided to make the cable termite and rodent proof. The thickness of the stainless steel alloy armour shall be > 0.125mm. The steel armour shall be both side coated with a copolymer of thickness > 0.05mm so as to bond the armouring to the outer jacket and make a unitary construction. Stainless steel shall be armouring corrugated transversely for lateral strength and bending flexibility to be applied longitudinally with an overlap of 10% (minimum) over the inner PE sheath. The corrugation over the entire length of the tape used in the cable shall be uniform, electrically continuous (applicable to all metallic elements used in the cable) and bonded to the outer sheath. The force of adhesion of the armour to the outer sheath shall be minimum 14 Newton and shall be tested as per ASTM:4565 test method. Suitable glue adhesive should be provided in between overlap portion of cable armouring for bonding to avoid ingress of moisture (below the armour). The height of the corrugation shall be 0.6mm (min.) and the pitch shall be 2.5mm(max.). Height and pitch of corrugation shall be measured between crest and tough base line. The corrugated armouring of stainless steel shall offer excellent corrosive resistance and shall be AISI Alloy no. 304 and the chemical composition and mechanical properties of steel shall be as specified in table 1 & 2 of ASTM : A167-92b for AISI 304 respectively.

20.50.10 The Outer Jacket

A non-metallic moisture barrier sheath (Red or Black in colour) shall be applied over the armour, which shall consist of tough weather resistance made of HDPE. The thickness shall be uniform and shall not be less than 2.0mm (Red in colour) for the cable having inner and outer HDPE sheath. The outer jacket shall have smooth finish and shall be termite resistant. The raw material and additive used to make the outer sheath termite proof shall be clearly mentioned by the manufacturer of the cable.

In case of HDPE material black in colour is used, the material from finished product shall be subjected to the following tests mentioned in Table 3  below;

| Table 3 |  |
| --- | --- |
| 1.Density | 0.94 to 0.965 gm/cc |
| 2.Melt flow index | < 0.8 gm/10 minutes at 1900 C |
| 3.Carbon black content | (2.5+0.5)% |
| 4.Carbon black Dispersion | Uniform dispersion |
| 5.ESCR | No crack till 48H in 10% Igepal solution 500C |
| 6.Moisture Content | <0.3% for 24H, ASTM D570 |
| 7.Tensile strength and Elongation at break | >2 Kg.mm2 and > 500% respectively |

Rip Cord: Suitable rip cord(s) shall be provided to open the outer sheath of the cable. The rip cord(s) shall be properly waxed to prevent wicking action and shall not work as a water carrier.

20.50.11 Mechanical Parameters & Tests: The offered cable shall meet requirement of mechanical characteristic & tests specified in this specification.

20.50.12   Cable drums, Marking, Packaging and Transport

All optical fibre cable shall be supplied on strong wooden drums provided with lagging with adequate strength, constructed to protect the cabling against all damage and displacement during transit, storage and subsequent handling during installation. The cable drum shall be suitable to carry underground fibre optic cable of required length. However, the exact lengths for drums to be supplied for each link shall be determined by the Contractor during detailed engineering/survey. Drum schedule shall be approved by the Employer before manufacturing the FO cable. Both cable ends in the drum shall be sealed and shall be readily accessible. The drum shall be marked with arrows to indicate the direction of rotation. Both the ends of the cable shall be provided with pulling eye. The pulling eye and its coupling system should withstand the same tensile load as applicable to the cable. The following marking shall be done on each side of the cable drums.

- Drum number

ii) 	Consignee’s name and address

- Contractor’s name and address

iv) 	Type of cable

v)	Number of fibres

vi)  	Type of fibres

vii) 	Year of manufacturing, month & batch no

viii) 	Name of manufacturer

ix) 	Total cable length

x) 	Inner end marking and Outer end marking

Packing list supplied with each drum shall have all the information provided on marking on the respective cable drum and following additional information: OTDR length measurement of each fibre and Ratio of fibre and cable length.

20.50.13 Optical fibre cable marking

A suitable marking shall be applied in order to identify this cable from other cables. Marking on the cable shall be indelible, of durable quality, shall last long and shall be applied at regular interval of one-meter length. Marking shall be imprinted and must clearly contrast with the surface and colours used must withstand the environmental influences experienced in the field. The accuracy of the sequential marking must be within + 0.5% of the actual measured length. The sequential length marking must not rub off during normal installation. In case laser printing is used the marking shall not exceed 0.15 mm depth. The optical fibre cable shall have the following markings in every meter.

i) 	Type of Cable

ii) 	Running meter length

iii) 	Number of fibres

iv) 	Type of fibre

v) 	Laser symbol & caution notice

vi) 	Year of manufacture and batch no.

vii)	 Manufacturer’s name

viii) 	Owner’s Name

20.50.14  Operating Instructions

Complete technical literature in English with detailed cable construction diagram of various sub-component with dimensions and test data of the cable shall be provided. All aspects of installation shall also be covered in the handbook.

20.50.15 Test and Inspection:

`Type Testing

The Bidder shall offer only the type tested cable and submit along with their bid the earlier carried out type test reports for the offered fibre optic cable meeting the requirement. The Contractor shall submit the previously carried out type test report for the same design of cable for the tests listed in Table  below. The fibre should have been type tested as per relevant International standards for the tests listed in Table below and the Bidder shall submit the test reports and certificates along with the bid. The Contractor shall submit the type test reports of fibres meeting the minimum requirement specified in Tables below.

Type Tests Fibre Optic Cable

TABLE-4

| S. No | Test Name | Test Procedure |
| --- | --- | --- |
| 1 | Water Ingres Test | (IEC 60794-1-F5/EIA 455-82B) Test duration:24 hours |
| 2 | Seepage of filling compound | (EIA 455-81A) Preconditioning: 72 hours, Test duration: 24 hours |
| 3 | Crush test | IEC 60794-1-E3/EIA 455-41) |
| 4 | Impact test | (IEC-60794-E4/ EIA 455-25A) |
| 5 | Stress strain Test | (EIA 455-33A) |
| 6 | Cable Cut-off wavelength | (EIA 455-170) |
| 7 | Temperature Cycling Test | (IEC60794-1-F1/EIA-455-3A)-2 cycles |

Type Tests Fibre Optic Cable

TABLE-5

| S. No | Test Name | Acceptance Criteria | Test Procedure |
| --- | --- | --- | --- |
| 1 | Attenuation | As per TS | IEC 60793-1-40 or EIA/TIA 455-78A |
| 2 | Attenuation Variation with wavelength |  | IEC 60793-1-40 or EIA/TIA 455-78A |
| 3 | Attenuation at Water Peak |  | IEC 60793-1-40 or EIA/TIA 455-78A |
| 4 | Temp Cycling (Temp dependence of Attenuation) |  | IEC 60793-1-52 or EIA/TIA 455-3A, 2 cycles |

| 5 | Attenuation with Bending (Bend Performance) |  | IEC 60793-1-47 or EIA/TIA 455-62A |
| --- | --- | --- | --- |
| 6 | Mode Field dia. | As per TS | IEC 60793-1-45 0r EIA/TIA 455-164A/167A/174 |
| 7 | Chromatic dispersion |  | IEC 60793-1-42 or EIA/TIA 455-168A/169A/175A |
| 8 | Cladding Diameter |  | IEC 60793-1-20 or EIA/TIA 455-176 |
| 9 | Point Discontinuities of attenuation |  | IEC 60793-1-40 or EIA/TIA 455-176 |
| 10 | Core-Clad concentricity error |  | IEC 60793-1-20 or EIA/TIA 455-176 |
| 11 | Fibre Tensile proof testing |  | IEC 60793-1-30 or EIA/TIA 455-31B |

Factory Acceptance Testing

The tests listed in Table below shall be carried out as Factory Acceptance Test for Underground fibre optic cable meeting the requirements specified in this section.

Factory Acceptance Tests on Underground Fibre Optic Cable

| Sl No | Factory Acceptance Test |
| --- | --- |
| 1 | Attenuation Coefficient (1310, 1550): By EIA/TIA 455-78A or OTDR |
| 2 | Point discontinuities of attenuation: By EIA/TIA 455-78A or OTDR |
| 3 | Visual Material verification dimensional checks as per approved drawings |

20.51	 PLB HDPE PIPE and ACCESSORIES

The following paragraphs describe the functional requirements, major technical parameters and Type and Factory Acceptance Testing requirements for Permanently Lubricant High Density Polyethylene (PLB HDPE) Pipe. PLB HDPE pipe shall be suitable for underground fibre optic cable installation by blowing as well as conventional pulling. The PLB HDPE pipe shall be suitable for laying in trenches by directly burying, laying through G.I/RCC hume pipe and laying through trench less digging. The expected service life of HDPE pipe and accessories shall not be less than 50 years. The unit rates quoted in the price schedule shall be the composite price of PLB HDPE pipe along with all accessories.

20.51.1 Construction of PLB HDPE pipe

The PLB HDPE pipe shall have two concentric layers viz. outer layer and inner layer. The outer layer shall be made of HDPE material and the inner layer of solid permanent lubricant. These concentric layers shall be co-extruded and distinctively visible in cross section under normal lighting conditions and generally conform to IS-9938. The colour of the PLB HDPE pipe shall be finalized during detail engineering. In the  finished PLB HDPE pipe, the co-extruded inner layer of solid permanent lubricant shall be continuous and integral part with HDPE outer layer and preferably be white in colour. The inner layer of solid permanent lubricant shall not come out during storage, usage and throughout the life of the pipe. The pipe shall be supplied in a continuous length of 1000 (one thousand) meter in coil form, suitable for transportation, installation and handling purposes. The finished pipe shall be of good workmanship such that the pipe is free from blisters, shrink holes, flaking, chips, scratches, roughness, break and other defects. The pipe shall be smooth, clean and in round shape, without eccentricity. The ends shall be cleanly cut and shall be square with axis of the pipe.

20.51.2 General

The HDPE pipe shall conform to the following standard and the technical specifications described in the following sections.

a) IS: 4984 / IS: 2530/IS:14151/(part1)/ IS:9938/IS:7328/IS12235(Part-9)/IS:5175

b) ASTM D 1693/ ASTM D 638/ ASTM D 648/ ASTM D 790 / ASTM D 1712/

ASTM D 2240/ ASTM D 4565 / ASTM F 2160/ ASTM G 154

c) TEC-spec no. GR/CDS-08/02/NOV-04(including all amendments)-HDPE pipe for

use as duct for optical fibre cable.

20.52 	Installation of Underground Fibre Optic Cable System

The Underground Fibre Optic Cable shall be installed along the power cable to be supplied & installed under this Project. This part of the section describes the installation procedures, installation of PLB HDPE pipes, installation of RCC hume pipes and GI Pipes, marking, backfilling, installation of underground FO cable, construction of manholes, splicing, termination and site acceptance testing requirements of the underground fibre optic cabling system.

20.52.4    Underground Fibre Optic Cable Installation

The cable shall be installed inside the 40mm diameter PLB HDPE pipe installed under this package along the route(s). Generally the cable shall be installed by compressed air blowing technique. However, for spans upto 150 meter, the Contractor can use pulling method for installation of OFC in HDPE pipe. If any temporary manhole or hand hole is required for installation of OFC, the same will be done by the Contractor without any additional cost implication. Adopting pulling method for installation of OFC for spans more than 150 meter, shall be subjected to approval of the Employer and shall be substantiated by proper justification. Contractor shall take into consideration the following guidelines, for installation of OFC approval by the Employer.

- The Optical Fibre Cable Drums shall be handled with utmost care. The drum shall not be subjected to shocks by dropping etc. They shall not be normally rolled along the ground for long distance and when rolled, shall in the direction indicated by the arrow. The battens shall be removed only at the time of actual laying.

- A blowing machine in association with an appropriate compressor shall be used for blowing.

- Temporary blowing chambers (if required) shall be constructed and then backfilled after blowing operation is completed.

- Locations along the route, which provide easy access points for blowing machine and   compressor, shall be determined.

- Before starting the cable blowing, PLB HDPE pipe shall be checked for obstacles or damage. Checking shall be done by using a proper sized mandrel.

- Always blow downhill wherever possible.

- Multiple blowing machines may be used in tandem if so required.

- Care must be taken not to violate the minimum bending radius applicable for the fibre optic cable. Tension in the cable during laying shall not exceed tension limit of the OFC. Installation by pulling may be permitted by the Employer only in specific cases where installation by blowing is not feasible on specific approval from the Employer. In case pulling is used, the pulling speed shall be determined considering the site condition. While installing the cable, excess length of about 10 meters shall be stored at each joint location for each side. Excess length of 10 m shall be kept at one ends of a road crossing culvert crossing and 20 meters at one end of bridges. However, exact excess lengths and manhole locations shall be finalised during detailed engineering depending upon the site requirement.

As Built Drawings/details

The Contractor shall submit the as built drawings for the whole route indicating the route, depth of digging and manhole locations for easy maintenance of the installed system.

List of Drawings/documents required to be submitted for Employer’s Approval

The Contractor shall ensure that the required drawings and documents are submitted well in time to avoid any delay in approval and project execution. The following minimum drawings and documents are required to be submitted by the Contractor for approval of the Employer:

a. 	The methods/procedures and the equipment/machines to be used for different types of trenchless digging techniques

b.	 Bill of quantities for various items as per contract

c.	 SAT Reports

d.	As built drawings

20.52.6       Site Acceptance Testing (SAT)

The tests, checks, adjustments etc conducted by the Contractor prior to offering the equipment/material for SAT shall be called Pre-SAT activities. During installation the Contractor shall maintain proper record of measurements in approved format and shall be given to the Owner/Employer (along with As Built drawing of the routes) for cross checking during SAT.

SAT for Excavation, Backfilling, Installation of Pipes, Manholes.

The tests shall include but shall not be limited to the following:

- Depth Check: One sample every 200 mtrs, Contractor shall prepare a sample pit at a location identified by the Employer. Depth of each item, warning tape, no. Of warning bricks (if applicable), pipes, cable etc. Shall be measured. Depth shall be as per technical specifications and shall correspond to recorded measurements.

- Crossings: 10% of each type, visual inspection for checking conformance with drawings, thickness of Concrete, RCC Hume Pipe and GI pipe.

- Manholes: As per technical specifications.

After inspection the Contractor shall backfill and carry out other restoration work at no additional cost to the Owner/Employer.

SAT for Underground Fibre Optic Cable

SAT for optical fibre cable shall be carried out link by link. Prior to installation, every fibre optic cable segment shall be tested for continuity and attenuation and measurements shall be recorded. Test requirements are as per table 2-7. Any discontinuity or attenuation beyond permissible limits in any of the fibres has to be recorded and brought to the notice of Employer. Upon completion of a continuous cable path, all fibres within the cable path shall be demonstrated for acceptance of the cable path. Test requirements are indicated in table 2-9 and in no case losses attributed due to other factors viz. Extra splice, kinks, will be acceptable to the limit determine by the following formula:

Max attenuation @ 1550 nm: 0.21dB/km + 0.05dB x total no of splices + 0.5dB x connector

Max attenuation @ 1310nm: 0.35dB/km + 0.05dB x total no of Splices + 0.5dB x connector

Any increase in attenuation or step discontinuity in attenuation shall not be acceptable and shall constitute a cable failure during installation. The Contractor shall have to either replace the concerned cable span at its own cost or provide additional splicing, joint box and manholes required to rectify the fault at its own cost. The fibre attenuation shall be tested again after replacement or rectification of fault. In case it is found that the splices are bad (loss is unacceptable as per approved test procedures), the Contractor shall have to do re-splicing and provide new Joint Box wherever required at no additional cost to the Owner/Employer. After re-splicing the end to end testing shall be repeated. The splice testing requirements are indicated in table below.

Table 6:     Fibre Optic Cable Pre-Installation Testing

| Item | Description |
| --- | --- |
| 1 | Physical Inspection of the cable assembly for damage |
| 2 | Optical fibre continuity and fibre attenuation with OTDR at 1550 nm |

Table 7 : Fibre Optic Cable Splice Testing

| Item | Description |
| --- | --- |
| 1 | Per splice attenuation with OTDR (bi-directional average) at 1550 nm |
| 2 | Physical inspection of Joint Box for proper fibre routing techniques |
| 3 | Physical inspection of sealing techniques, weatherproofing, etc |

Table 8: Fibre Optic Cable Commissioning Testing

| Item | Description |
| --- | --- |
| 1 | Fibre continuity and link attenuation (bi-directional) for each fibre at 1310 &1550 nm by OTDR |
| 2 | Fibre continuity and link attenuation (bi-directional) for each fibre at 1310 &1550 nm by Power Meter & Laser Source |
| 3 | Average splice loss (bi-directional) for each splices and average splice loss for the link by OTDR at 1550 nm. |

SAT for PLB HDPE pipe

For PLB HDPE pipes, duct integrity tests shall be carried out as described below. The Duct cleaning (Sponge test) test shall be carried out on all the ducts before blowing/pulling of the cable between two consecutive manholes on the PLB HDPE pipes.

Duct cleaning (Sponge test)

Compressed air should be blown through the PLB HDPE pipe in order to remove dirt and water, if any, with the help of suitable Air Compressor. A short blast of air about 2-3 Bar shall be blown through the PLB HDPE pipe for about 2 minutes. Sponge shall be blown through the duct to thoroughly clean the duct from inside.

Crush and deformity test

Place a shuttle of length <15cm and O.D. 80% of the inner diameter of the offered PLB HDPE pipe. Connect the compressor pipe with a suitable flexible wire grip at the other end to catch the shuttle and start blowing operation to the pipe and check if shuttle reaches at the other end. If shuttle gets stuck the Contractor shall adopt suitable arrangement at site to locate the deformity/damage in the HDPE pipe, repair the pipe and ensure end-to-end continuity of the duct in sound condition.

20.52.7	     Documentation

Apart from survey reports as mentioned above, the Contractor will submit the following documents after completion of the job and acceptance by the Employer:

- As built drawing of the route indicating the distance from road centre, OFC drum length, location of other utilities, link Q, OFC loop length, name of the road, sections and positions of PLB HDPE pipes, couplers, warning bricks/stone, manholes, G.I. pipes, RCC pipes, joint box, conduits, bends, trays, optical fibre cable loop lengths in manholes etc.

(b) 	Depth of PLB HDPE pipe in various sections of the route executed through open trenching.

(c) 	Sections of trenching digging executed through various methods.

(d) 	Specific deviation w.r.t. the installation and supply items, if any, from the technical specification. If there is no deviation, either explicit or implicit, the Contractor will provide a certification to this effect.

(e) 	Without submission of the above documentations, the Site Acceptance Testing of various items as described above will be deemed to be incomplete.

20.52.8 	Miscellaneous Jobs

In order to provide end-to-end connectivity, it may be required to execute some miscellaneous jobs as detailed below.

Routing of Cables inside building.

In order to route the OFC (Optical Fibre Cable) from the underground trench to the control room building it is necessary to install the cable on walls inside PLB HDPE pipe over the existing cable tray/raceways inside the building.

Installation of PLB HDPE pipe on wall

The PLB HDPE pipe may be required to be installed on the wall using steel or G.I clamps. The contractor will provide the required clamps and other consumables sufficient for such installation. The contractor will take care of aesthetics while installation. The OFC will be pulled through the PLB HDPE pipe with due care as described in relevant Para of this specification.

20.52.9 	INSPECTION & TESTING

Type Testing

Bidder shall offer the type tested product meeting the requirement of technical specifications.

Factory Acceptance Tests

Factory acceptance tests shall be conducted on randomly selected final assemblies of all equipment to be supplied. Visual inspection shall be carried out on 100% basis for all the equipment/items offered. Factory acceptance testing shall be carried out on Underground fibre optic cable, Joint box, PLB HDPE pipe etc.

20.52.10	System Maintenance

The one year period commencing immediately after the operational acceptance is called the Defect liability Period/warranty period. Operational Acceptance shall be given on successful completion of SAT. During this period, the Contractor shall replace or repair all defective parts. The one year period commencing immediately after the operational acceptance is called the Warrantee Period/Defect Liability Period. During the Warranty Period/Defect Liability Period, the Contractor shall guarantee that there shall be minimum outage of the supplied system. During this period, the Contractor shall replace or repair all defective parts and shall have prime responsibility for maintaining an operational system.

20.52.11     	Documentation

The documentation provided shall include the following:

(a) Detailed list of the deliverables

(b) Description of the products

(c) 	Technical particulars

(d) 	Installation manuals

(e)	 Maintenance manuals

(f) 	Quality assurance manuals, Manufacturing Quality Plan (MQP) & Field Quality

20.53 SPECIFIC TECHNICAL PARTICULARS FOR 33 KV XLPE CABLE

| Sl.No. | Particulars | Details |
| --- | --- | --- |
| 1 | Description of Cable | ARMOURING: ARMOURED CORE MATERIAL: COPPER INSULATION: XLPE NOMINAL AREA: As per BoQ. NO.OF CORE: Single Core SHEATHING MATERIAL: EXTRUDED PVC, INNER & OUTER VOLTAGE GRADE: 33KV |
| 2 | Highest system voltage | 36 KV |
| 3 | Voltage Grade | 19/ 33KV |
| 4 | Earthing System | Effectively earthed |
| 5 | Frequency | 50 Hz |
| 6 | Size of Cable | As per BoQ |
|  | No. of Core | 1C |
| 7 | Rated Power Frequency Withstand Voltage (1 min) | 70 KV (rms) |
| 8 | Impulse withstand BIL (1.2/ 50/ micro Sec) Line to earth | ±170 kVp |
| 9 | Rated short time withstand current | 31.5 KA (rms) for 1 sec |
| 10 | Rated peak withstand current (1 sec) | 78.75 KA |
| 11 | No of phase per Ckt | 3 |
| 12 | Maxm.Conductor temp | 90 degree C at maxm. continuous current |
| 13 | Maxm. Permissible short circuit Temperature | 250 degree C for one second |
| 14 | End Sealing | H.S. Caps |
| 15 | CABLE DETAILS : CONDUCTORS |  |
| i | Conductor material | Plain un-tinned annealed copper |
| ii | Conductor Shape | Compacted circular. |
| iii | Conductor Screen | Extruded, Cross-linked, semi conducting compound of suitable thickness. Semi conducting separator tapes with 50% overlap to be applied between conductor and conductor screen. |
| iv | Resistivity of the semiconducting screen | Maximum 1000 ohm-meter |
| 16 | INSULATION |  |
| i | Insulation material | XLPE |
| ii | Insulation thickness | 8.8 mm (Nominal thickness) |
| iii | specified insulation resistance at 900C | 1x1012 ohm cm |
| iv | Insulation Screen: Type & Material | Freely strippable (with heat) type extruded non-metallic semi conducting compound followed by copper metallic tape with minimum 25 % overlapping. |
| 16 | Resistivity of the semiconducting compound | Max 500 Ohm-meter |
| 17 | Longitudinal water barrier Material | Layer of semiconducting tape with suitable water swellable absorbent with 50% overlap. |
| 18 | Overall sheath | Extruded black HDPE (TypeST7) with anti termite and anti rodent treatment. |
| 19 | Coating of outer sheath | A hard baked layer of graphite or semi conducting layer shall be applied over the outer sheath as outer electrode for testing the sheath. |
|  | Armouring | Armoured |
| 20 | TESTS |  |
| i | Type Test | All tests as per specifications IEC Standards. |
| ii | Routine Test | All tests as per specifications IEC Standards. |
| iii | Acceptance Test | All tests as per specifications IEC Standards. |
| iv | Whether test will be witnessed by purchaser or his representative | Yes. Acceptance test will be witnessed. |
| 21 | Bending Radius | The minimum bending radius of XLPE insulated cables as follows: Cable: Bending radius Single Core: 25xD D – diameter of overall conductor. |

20.54 SPECIFIC TECHNICAL PARTICULARS FOR 66KV, 132 KV & 220KV XLPE CABLE

| Sl.No. | ITEMS | PARTICULARS |
| --- | --- | --- |
| 1 | Description of Cable | Stranded single core compacted copper core screening by a layer of semi conducting tape followed by a layer of semiconducting compound as conductor screen, XLPE insulation, insulation screening with semiconducting compound extruded directly over the insulation, (semiconducting conductor screen, XLPE insulation, semiconducting insulation screen-all in one triple extrusion process), longitudinal sealing by a layer of water swellable semiconducting non woven tape over insulation screen, followed by radial sealing (metal sheath of Corrugated Aluminum),and overall extruded black HDPE Sheathed (TypeST7). |
| 2 | Highest system voltage | 72.5KV 145KV 245KV |
| 3 | Voltage Grade | 36/66KV 76/132KV 127/220KV |
| 4 | Voltage variation | +10% and -12.5% |
| 5 | Frequency | 50 Hz |
| 6 | Frequency variation | ±3% |
| 7 | Power frequency withstand voltage | 90KV rms for 30 minutes 190 KV rms for 30 minutes 318KV for 30 minutes |
| 8 | Lightning impulse withstand voltage | ±325KVpeak 650KVpeak 1050peak |
| 10 | No of phase per Ckt | 3 |
| 11 | Earthing system | Effectively earthed |
| 12 | Size of Cable | As per BoQ |
| 13 | Max. in Conductor Temp. | 90ºC at maximum continuous current. |
| 14 | Fault level | 31.5KA for 1 second 40Ka for 1 second 50KA for 1 second (considering parallel path of lead sheath and screen copper for metallic screen) |
| 15 | Maximum permissible short ckt temperature. | 250ºC for one second. |
| 16 | CABLE DETAILS : CONDUCTORS |  |
| 16.1 | Conductor material | Plain un-tinned annealed copper. |
| 16.2 | Conductor Shape | Compacted circular. |
| 16.3 | Conductor Screen | Extruded, Cross-linked, semi conducting compound of suitable thickness. Semi conducting separator tapes with 50% overlap to be applied between conductor and conductor screen. |
| 16.4 | Resistivity of the semiconducting screen | Maximum 1000 ohm-meter |
| 16.5 | Insulation |  |
|  | a)material | XLPE |
|  | b)specified insulation resistance at 900C | 1x1012 ohm cm |
| 16.6 | Insulation Screen: Type & Material | Extruded semi conducting compound. |
| 16.7 | Resistivity of the semiconducting compound | Max 500 Ohm-meter |
| 16.8 | Longitudinal water barrier Material | Layer of semiconducting tape with suitable water swellable absorbent with 50% overlap. |
| 16.9 | Radial moisture barrier Material | Seamless or seam welded Corrugated Aluminum sheath with anti-corrosive material. |
| 16.10 | Overall sheath | Extruded black HDPE (TypeST7) with anti termite and anti rodent treatment. |
| 16.11 | Coating of outer sheath | A hard baked layer of graphite or semi conducting layer shall be applied over the outer sheath as outer electrode for testing the sheath. |
| 17. | Approximate Length of cable in a drum | 500 metres with a tolerance range of ±5% or as per requirement. |
| 18 | Bending Radius | The minimum bending radius of XLPE insulated cables as follows: Cable: Bending radius Single Core: 25xD D – diameter of overall conductor. |
| 19 | TESTS Applicable standards | IEC60840 IEC62067 |
| 19.1 | Type Test a)whether previous test reports will be sufficient b)whether sample to be Type tested against this order. | All tests as per specifications IEC Standards Yes, if done on identical cable. No, if done on identical cable. |
| 19.2 | Routine Test | All tests as per specifications IEC Standards. |
| 19.3 | Acceptance Test | All tests as per specifications IEC Standards. |
| 19.4 | Whether test will be witnessed by purchaser or his representative | Yes. Acceptance test will be witnessed. |
| 20 | INSTALLATION, TERMINATION AND JOINTS |  |
| 21 | Ambient temperature Ground temperature Thermal resistivity of soil | 450C 300C 1500C cm/Km |
| 22 | Laying Configuration | Trefoil formation. |
| 23 | Depth | 1.5 m below ground level. |
| 24 | Termination |  |
| 25 | Type | AS per requirement |
| 26 | Joints Required | No |
| 27 | Earth Link Boxes Required | Yes. In both end and at joints as per cable bonding system |
| 28 | Surge Suppressor Required | Yes |
| 29 | Type Bonding ‘ | Single end bonding/ cross bonding |