CHAPTER 37: SCOPE AND GENERAL TECHNICAL CONDITION FOR TRANSMISSION LINES

##### A. Nature of work

The work covered by this Specification is for 400 kV and/or 220 kV and/or 132 kV transmission lines as specified herein and in the attached Schedules. The overhead transmission lines will form part of the AEGCL Transmission System.

- B. General particulars of the system

The following are the general particulars governing the design and working of the complete system of which the Works will form a part —

- Electrical energy is generated at interconnected power stations as three-phase current at a frequency of 50 Hz, and transmitted therefrom by means of overhead lines.

- The system will be in continuous operation during the varying atmospheric and climatic conditions occurring at all seasons as mentioned in chapter 2 of this bidding document.

37.1.0 SCOPE-

Construction of 400 KV, 220 KV and 132 KV

As indicated in the Bidding Proposal Sheet & scope of work.

Important: For obtaining Right of way (ROW) the contractor shall refer to Scope of the work of the bidding document Volume-I

37.2.0      SURVEY (detail & check, estimating of quantities & spotting of towers)

37.2.0.1    General: Preliminary route alignment in respect of the proposed transmission lines has been fixed by the employer subject to alteration of places due to way leave or other unavoidable constraints. The Right of way shall be solved by the contractor and all expenses there of shall be paid by the contractor, which will be reimbursed by AEGCL time to time. However, AEGCL shall render all helps in co- ordination with law and order department for solving the same. Forest clearance if any shall be arranged by AEGCL.

    - Provisional quantities/numbers of different types of towers have been estimated and indicated in the BOQ Schedule given. However final quantities for work shall be as determined by the successful bidder, on completion of the detail survey, preparation of route profile drawing and designing of the different types of towers as elaborated sin the specification and scope of work.

    - The contractor shall undertake detailed survey on the basis of the tentative alignment fixed by the employer. The said preliminary alignment may, however, change in the interest of economy to avoid forest and hazards in work. While surveying the alternative route the following points shall be taken care by the contractor.

        - The line is as near as possible to the available roads in the area.

        - The route is straight and short as far as possible.

        - Good farming areas, religious places, forest, civil and defence installations, aerodromes, public and private premises, ponds, tanks, lakes, gardens, and plantations are avoided as far as practicable.

- The line is far away from telecommunication lines as reasonably possible. Parallelism with these lines shall be avoided as far as practicable.

        - Crossing with permanent objects are minimum but where unavoidable preferably at right angles.

- Difficult and unsafe approaches are avoided.

- The survey shall be conducted along the approved alignment only in accordance with IS: 5613 (Part-II/Section-2), 1985.

- For river crossing/ Crossing of Nallas: Taking levels at 20 metre intervals on bank of river and at 40 metre intervals at bed of river so far as to show the true profile of the ground and river bed. The levels may be taken with respect to the nearest existing towers, pile foundation of towers, base or railway/road bridge, road culvert etc. The levels shall be taken at least 100 m. on either side of the crossing alignment. Both longitudinal and cross sectional shall be drawn preferably to a scale of 1:2000 at horizontal and 1:200 vertical.

- After completing the detailed survey, the contractor shall submit the final profile and tower schedule for final approval of the employer. The final profile and tower schedule shall incorporate position of all type of towers. To facilitate checking of the alignment, suitable reference marks shall be provided. For this purpose, concrete pillars of suitable sizes shall be planted at all angle locations and suitable wooden/iron pegs shall be driven firmly at the intermediate points. The contractor shall quote his rate covering these involved jobs.

- Only approved sag template shall be used for tower spotting and the final profiles. However preliminary survey has been done by AEGCL and any further survey required shall be done by the contractor.

      - PROFILE PLOTTING AND TOWER SPOTTING

37.2.0.4.1 The profile shall be plotted and prepared to the scale 1 in 2,000 for horizontal and 1 in 200 for vertical on squared (mm) paper. If somewhere the difference in levels be too high, the chart may be broken up according to the requirements. A 10 mm overlap shall be shown on each following sheet. The chart shall progress from left to right for convenience in handling. The sheet size may be conveniently chosen.

37.2.0.4.2 With the help of sag template, final tower location shall be marked on the profiles and while locating the tower on survey chart, the following shall be kept in mind:

The contractor shall also submit the land schedule on revenue (if required) maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval. Detail GIS (Geographical Information System) of towers to be included.

37.2.0.4.3 The number of consecutive spans between the section points shall not exceed 10 in case of straight run on a more or less plain stretch.

37.2.0.4.4 Individual span shall be as near as to the normal design ruling span.

37.2.0.4.5 In different crossing the contractor shall take into consideration the prevailing regulations of the respective authorities before finalizing type and location of the towers. While carrying out survey work, the contractor has to collect all relevant data, prepare and submit drawings in requisite number for obtaining clearance from the PTCC, road, aviation, railways, river and forest authorities.

37.2.0.4.6 The contractor shall remain fully responsible for the exact alignment of the line. If after erection, any tower is found to be out of alignment, the same shall have to be dismantled and re- erected after correction by the contractor at his own cost, risk and responsibility, including installation of fresh foundation, if belt necessary by the employer.

37.2.0.4.7 After peg marking of the angle tower or tension towers, the contractor shall obtain approval from the employer and thereafter pegging of suspension type tower shall be done by the contractor and pegging of all the four legs of each type of towers at all the locations shall be done.

    - SCHEDULE OF MATERIALS

When the survey is approved, the contractor shall submit to the employer a complete detail schedule of all materials to be used in the line. Size and length of conductor etc. are also to be given in the list. This schedule is very essential for finalizing the quantities of all line material. The contractor shall furnish the same.

37.2.1 DETAILED SURVEY/CHECK SURVEY:

The contractor will have to carry out detailed survey of the line for which route map indicating the proposed alignment of the transmission line will be handed over by the Employer. If the detailed survey is already conducted by the Employer for some portion of the line, the profiles for such portion will be handed over to the Contractor for carrying out check survey. It may please be noted that no check survey is required to be conducted for the portion of line for which detail survey is conducted by the contractor himself.

- Detailed Survey:-

(a) At the starting point of the commencement of route survey, an angle iron spike 65 x 65 x 1000mm shall be driven firmly into the ground to show only 150mm above the ground level. A punch mark on the top section of the angle iron shall be made to indicate location of the surveying instrument. Teak wood pegs 50 x 50 x 650 mm shall be driven at prominent positions at intervals of not more than 750 meter along the transmission line to be surveyed up to the next angle point. 125 mm wire nails should be fixed on the top of these pegs to show the location of instrument. The pegs shall be driven firmly into the ground to show only 100 mm above ground level. At angle positions, stones shall be put up for easy identification. Paint mark in white lead paint shall be put in, about 300 mm squares with a direction indication, on nearby boulders, rocks, or trees, along the complete line alignment. At peg position, identification marks giving the peg position, with reference to painting marks, shall be given. The white lead paint mark shall indicate to the individual the direction of alignment from either direction.

(b) Routing/Re-routing of transmission line through protected/reserved forest area

should be avoided. In case it is not possible to avoid the forests or areas having large trees completely, then keeping in view of the overall economy, the route should be aligned in such a way that cutting of trees is minimum.

(c) The route should have minimum crossings of Major river, Railway lines, National/State highways, overhead EHV power line and communication lines.

(d) The number of angle points shall be kept to minimum.

(e) The distances between the terminal points specified shall be kept shortest possible, consistent with the terrain that is encountered.

(f) Marshy and low lying areas, river beds and earth slip zones shall be avoided to minimize risk to the foundations.

(g) It would be preferable to utilize level ground for the alignment.

(h) Crossing of power lines shall be minimum. Alignment will be kept at a minimum distance of 300 m from power lines to avoid induction problems on the lower voltage lines.

(i) Crossing of communication line shall be minimized and it shall be preferably at right angle. Proximity and parallelism with telecom lines shall be eliminated to avoid danger of induction to them

(j) Areas subjected to flooding such as nalah shall be avoided.

(k) Restricted areas such as civil and military airfield shall be avoided. Care shall also be taken to avoid aircraft landing approaches.

(l) All alignment should be easily accessible both in dry and rainy seasons to enable maintenance throughout the year.

(m) Certain areas such as quarry sites, tea, tobacco and saffron fields and rich plantations, gardens and nurseries which will present the Employer problems in acquisition of right of way and way leave clearance during construction and maintenance should be avoided.

(n) Angle points should be selected such that shifting of the point within 100 m radius is possible at the time of construction of the line.

(o) The line routing should avoid large habitations, densely populated areas, Forests, Animal/Bird sanctuary, reserve coal belt areas, oil pipe, line/underground inflammable pipe lines etc to the extent possible.

(p) The areas requiring special foundations and those prone to flooding should be avoided.

(q) From the field book entries, the route plan and level profile shall be plotted and prepared to the scales of 1:2000 horizontal and 1:200 vertical on 1 mm/5 mm/1 cm square paper.

(r) If the difference in levels be too high, the chart may be broken up according to requirement. A 400 meter overlap shall be shown on each following sheet. The chart shall progress from left to right. For convenience in handling, the sheet size may be limited to 594x841 mm (Al) size.

(s) After completing the detail survey, profiles shall be submitted to the Employer duly spotted with tower for approval. While submitting the profiles after conducting the detail survey, the contractor will also submit a copy of route alignment on the route map indicating the surveyed route.

- Check Survey:

(a) The Contractor shall conduct the check survey after the profiles are handed over to the Contractor. The check survey shall include checking of deviation angles, checking of levels at critical points. After completing the check survey, the tower spotting shall be carried out by the Contractor and profiles shall be submitted to the purchaser for final approval. The Contractor shall be responsible for correct setting of stubs. Discrepancies, if any, shall be brought to the notice of purchaser and final approval shall be taken before execution of work.

(b) The requirement of tower site levelling and revetment work, if required, shall also be marked by the Contractor on the profiles while carrying out the detail or check survey work.

(c) If due to site conditions any change in the tower location/provision of extension is considered necessary compared to approve profiles, the contractor shall bring the same to the knowledge of the purchaser well in time and get revised approval of the profile before setting the stubs. The revised approval shall be conveyed to the Contractor by the Purchaser.

- Soil Resistivity:-

While carrying out detailed/ check survey work, the Soil Resistivity values will have to be measured at convenient points along the route, not exceeding 2.50 Km between adjacent points. The Soil Resistivity will be measured using 4 electrode method with an inter electrode spacing of 50 M.

The following formula shall be used:

P = 2 π a R

Where a = Interelectrode spacing = 50M

R = Earth resistance measured in Ohms

P = Soil Resistivity in Ohm- m

The soil resistivity values shall be submitted duly marked on the route map and also in the form of statement. The quoted rates for detailed survey/ check survey work shall be inclusive of cost of measuring soil resistivity values along the proposed route and the contractor will not be paid separately for this work.

- RIGHT OF WAY (ROW)

The contractor shall refer to chapter 2 of this bidding document for obtaining ROW.

37.2.2 SUB-SOIL INVESTIGATION

To ascertain soil parameters in various stretch, inter, the contractor shall carry out sub-soil investigation through reputed soil consultant as approved by the employer.

37.2.2.1 SCOPE OF WORK

The scope of sub-soil investigation covers execution of complete soil exploration for the transmission line under this contract including boring, drilling, collection of undisturbed soil sample where possible, otherwise disturbed samples, conducting laboratory test of soil samples to find out the various parameters as detailed in this specification and submission of detailed reports in 6 copies along with specific recommendation regarding suitable type of foundation for each bore-hole along with recommendation for soil improvement where necessary.

37.2.2.2 QUALIFYING REQUIREMENTS OF SOIL CONSULTANTS

The soil consultants shall provide satisfactory evidence concerning the following as and when asked for. That, he/they has/have adequate technical knowledge and previous practical experience in carrying out complete soil investigation jobs in any kind of soil. That he/they has/have well equipped, modernized soil testing laboratory of his/their own. If asked for by the employer, the contractor shall arrange inspection of such laboratory of the soil consultant by the representative of the employer. If in the opinion of the employer, the soil consultant (proposed by the contractor) is not well equipped or capable to undertake the sub-soil investigation job relating to this contract, then such soil consultant shall not be engaged to undertake the job. In that case, they shall have to engage other agency as will be approved by the employer.

37.2.3  TEST BORING

The boring shall be done at the major locations/crossing, special towers. However, it is desirable that there should be at least one sub-soil investigation bore-hole for the line. Such locations for sub-soil investigation shall be selected and finalized in consultation with the employer.

The test boring through different layers of all kinds of soil shall have to be carried out by the contractor through the approved soil consultant as briefed hereunder.

- Method of boring, selection of sampling tubes, sampling, recording of boring, protection, handling, leveling of samples shall be done as specified in IS: 1892/1977, if any, after obtaining approval from the employer. The contractor/consultant shall furnish in the soil report in details, the equipment and method of boring actually adopted.

- Depth of boring below ground level shall be 15 M. only unless continuous bedrock is encountered earlier. In case rock is encountered at any depth within 15 M. adequate study of rock and assessment of strength characteristics shall be done and recommendation shall be given.

- Undisturbed soil samples shall be obtained for the initial 4M depths at every 1.5M interval and at change of strata. After these initial 4M depths, samples shall be obtained preferably at every 3M or where there is a change of strata, or as advised by the employer.

- In case collection of undisturbed samples becomes difficult/impossible detailed soil testing on remoulded soil samples is to be considered and reported in the soil report.

- Standard penetration test as per IS: 2131 with latest amendment shall have to be conducted in different strata and recorded properly.

- The ground water table shall be recorded during boring operation and incorporated in the bore log. If possible, the position of the water table just after monsoon period be ascertained from local people and indicated in the report.

- Plate Load test shall have to be conducted at special tower location.

37.3.0	LABORATORY TESTS OF SOIL SAMPLES

The method and procedure of testing of soil sample to be followed shall be as per relevant IS codes. Adequate volume of test samples shall be collected from site. Ample shall be properly sealed immediately after recovery as specified in relevant IS code and transported carefully to laboratory for carrying out necessary laboratory tests to find out the following parameters of every samples. Data and time of taking of the sample shall be recorded in the test report.

- Natural moisture content, Liquid limit, Plastic limit and Plasticity index.

- Bulk, dry and buoyant density of soil.

- Void ratio (e-long P curve shall be submitted)

- Specific gravity.

- Grain size distribution (Sieve analysis and hydrometer analysis)

- Tri-axial and consolidation tests (consolidation undrained and consolidated drained as and when application in table, graph and drawing.

- Permeability tests

- Chemical tests for both water and soil samples at different layers.

- Evaluation of safe bearing capacity at different strata for square footings shall be done for a maximum value of 25-mm. settlements.

- At depts. From 3M to 10M be different strata.

- Factor of safety shall be considered as 3 for evaluation of safe bearing capacity of soil.

- Unconfined compression test for cohesive soil (=0) if encountered.

    - REPORT ON SUB-SOIL INVESTIGATION

The contractor shall make analysis of soil samples and rock cores as collected by him in the field and approved by the employer as collected by him in the field and approved by him in the field and approved by the employer as well as field tests and laboratory tests. A comprehensive report shall have to be prepared by him, finally incorporating all the data collected in proper tabular forms or otherwise along with the analysis.

The 3(three) copies of report in the draft form shall be submitted for employer’s approval. 6(six) copies of final report incorporation employer’s comments, if any shall be submitted within 3(three) weeks after completion of this work.

Recommendations shall include but not be limited to the following items (a) to (p)

- Geological information of the region.

- Past observations and historical data, if available, for the area or for other areas with similar profile or for similar structures in the nearby area.

- Procedure of investigations employed and field and field as well as laboratory test results.

- Net safe bearing capacity and settlement computation for different types of foundations for various widths and depths of tower.

- Recommendations regarding stability of slopes, during excavations etc.

- Selection of foundation types for towers.

- Bore hole and trial pit logs on standard proforma showing the depths, extent of various soil strata etc.

- A set of longitudinal and transverse profiles connecting various boreholes shall be presented in order to give a clear picture of the site, how the soil/rock strata are varying vertically and horizontally.

- Modulus of sub grade reaction from plate load test for pressure ranging up to 6 kg/cm. The recommended values shall include the effect of size, shape and depth of foundations.

- Deformation modulus from plate load test in various test depth/stratification.

- Coefficient of earth pressure at rest.

- Depth of ground water table and its effect on foundation design parameters.

- Recommendations regarding stability of slopes, during shallow excavation etc.

- Whether piles are necessary or not. If piles are necessary, recommendation of depth, diameter and types of piles to be used.

- Recommendations for the type of cement to be used and any treatment to the underground concrete structure based on the chemical composition of soil and sub-soil water.

    - MEASUREMENT OF SOIL RESISTIVITY

For the purpose of grounding design, soil resistance measurement shall be taken in the locations as stated under clause 1.0 above and based on which the value of soil resistance shall be derived. Wenner’s four (4) electrode method shall be used for earth resistance measurement in accordance with the procedure and the calculation detailed in IS:3043 1987. At least 8(eight) test direction shall be chosen from the center of the locations to cover the whole site. The employer reserves the right to carry out separate soil investigation at his cost by engaging a separate agency for cross checking the result obtained by the contractor. In case the results are at variance, the soil parameters to be adopted for final design will be at the sole discretion of the employer and such will be binding upon the contractor.

IMP:-The material and services covered under these specifications shall be performed as per requirements of the relevant standards and codes referred hereinafter against each set of equipment and services. In case of a conflict between such codes and/or standards and the Specifications, the latter shall govern. Other Internationally acceptable standards which ensure equal or higher performance than those specified shall also be accepted.

---------------------------------------------------------------------------------------------------

SL.	Indian	Title	 International &

No.	Standards	 Internationally

recognised Standards.

------------------------------------------------------------------------------------------------

| 1 |  | IS 209-1979 | Specification for zinc | ISO/R/752-1968 ASTM B6 |
| --- | --- | --- | --- | --- |
| 2 |  | IS 269-1976 | Structural Steel (standard quality) | ISO/R/630-1967 CAN/CSA G40.21 BSEN 10025 |
| 3 |  | IS 269-1976 | Ordinary rapid hardening and low heat Portland cement | ISO/R/597-1967 |
| 4 |  | IS 383-1970 | Coarse and fine aggregates from natural sources for concrete | CSA A23.1/A23.3 |
| 5 | a | IS 398-1982 | Specification for aluminium conductor for overhead transmission purpose | IEC 1089-1991 Part I BS 215-1970 |
|  | b | IS 398-1982 | Aluminium conductor galvanized steel reinforced | BS 215-1970 Part-II, IEC 1089-1919 |
|  | c | IS 398-1994 | Aluminium alloy | BS 3242-1970 |

|  |  |  | Part-IV |  | stranded conductor | IEC 1089-1991 ASTM 8393M86 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | d) | IS 398-1982 Part-V |  | Aluminium conduc- tor galvanised steel reinforced for Extra High Voltage (400kV and above) | BS 215-1970 IEC 1089-1991 |  |
| 6. |  |  | IS 278-1978 |  | Specification for barbed wire. | ASTM A 121 |  |
| 7. |  |  | IS 406-1964 |  | Method of chemical analysis of Zinc slab |  |  |
| 8. |  |  | IS 432-1966 (Part 1 & 11) |  | Mild steel and medium tensile bars and hard drawn steel wire for concrete reinforcement. | BS 4449 CSA G-30. BS 4482 |  |
| 9. |  |  | IS 456-1978 |  | Code of practice for plain and reinforced concrete. | ISO 3893-977 |  |
| 10. |  |  | IS 731-1971 |  | Porcelain insulators for overhead power lines with nominal voltage greater than 1000 Volts. | BS 137-1982 (Part-I & II ) IEC 383-1993 (Part-I& II ) |  |
| 11 |  |  | IS 800-1962 |  | Code fo practice for use of structural steel ingeneral building construction | CSA S 16.1 BS 5950 |  |
| 12. a) |  | IS802-(2015) part 1/section 1 |  | Code of practice for use of structural steel in overhead transmission Line: materials, loads and permissible stresses |  |  | IEC 826 ANSI/ASCE 10-90 (1991)BS 8100 |
| b) |  | IS802-(2016) (Part-I/ section 2) |  | Code of practice for use of structural steel in overhead transmission line, fabrication, galvanising inspection and packing |  |  | ANSI/ASCE 10-90 (1991) |
| c) | IS 802-Part3 |  |  | Code of practice for use of structural steel in over-head transmission lines towers: testing |  |  | ANSI/ASCE 10-90 (1991) (Part III) IEC 652 |
| 13 IS 1139-1966 |  |  |  | Hot rolled mild steel, medium tensile steel hogh yield strength deformed bars for concrete reinforcements |  |  | CAN/CSA G30.18 ASTM A615 and BS 4449 |
| 14 IS 1367-1967 |  |  |  | Technical conditions for threaded fastners |  |  |  |
| 15 IS 1489-1976 |  |  |  | Portland pozzolana cement |  |  | ISO/R 863-1968 |
| 16 IS 1521-1972 |  |  |  | Method of tensile testing of steel wires |  |  | ISO 6892-1984 |
| 17 IS 1573-1976 |  |  |  | Electroplated coating of zinc on iron and steel |  |  | BS-1559-194 |
| 18 IS 1786-1966 |  |  |  | Cold twisted steel bars for concrete reinforcement |  |  |  |
| 19 IS 1778-1980 |  |  |  | Reels and drum for bare conductro |  |  |  |
| 20 IS 1893-1965 |  |  |  | Criteria of earthquake resistant design of structures |  |  | IEEE 693 |
| 21 IS 2016-1967 |  |  |  | Plain washers |  |  | ISO/R 887-1968 ANSI B18.22.1 |
| - IS 2071 Part-I-1974 Part-II-1974 Part-III-1976 |  |  |  | Method of high voltage tesings |  |  | IEC 60 |
| - IS 2121 - part - Part-1981 |  |  |  | Specification for conductor and earthwire accessories for overhead power lines |  |  |  |

|  | - Part-I-1981 - Part-II -1981 - Part-III-1992 - Part-IV-1991 | Armour rods, binding wires and tapes for conductors. Mid-span joints and repair sleeve for conductors. Accessories for earthwire. Non-tension joints. | ASTM D 1 883 |
| --- | --- | --- | --- |
| 24. | IS 2131-1967 | Method of standard penetration test for soils. |  |
| 25. | IS 2551-1982 | Danger notice plates |  |
| 26. | IS 2486 | Specification for insulator fittings for overhead power lines with a nominal voltage greater than 1000 Volts. |  |
|  | Part-I | General requirements and tests. | BS 3288 IEC 1284 |
|  | Part-II | Dimensional requirements | IEC 120-1984 |
|  | Part-III | Locking devices | IEC 372-1984 |
| 27. | IS 2629-1966 | Recommended practice for hot dip galvani- sing of iron and steel. | ASTM A123 CAN/CSA G 164 BS 729 |
| 28. | IS 2633-1972 | Method of testing uniformity of coating of zinc coated articles. | ASTM A123 CAN/CSA G164 |
| 29. | IS 3043-1972 | Code of practice for earthing(with amend- ment No.1 and 2). |  |

| 30. | IS 3063-1972 | Single coil rectangular DIN 127-1970 section spring washers for bolts nuts, screws. |  |
| --- | --- | --- | --- |
| 31. | IS 3188-1965 | Dimensions for disc IEC 305-1978 insulators. |  |
| 32. | IS 4091-1967 | Code of practice for ASCE/IEEE 691 design and construction of foundation for transmission line towers and poles. |  |
| 33. | IS 4826-1979 | Galvanised coating on round steel wires. | IEC 888-1987 BS 443-1982 |
| 34. | IS 5358-1969 | Hot dip galvanised coat- ings on fasteners. | CAN/CSG 164 ASTM A153 |
| 35. | IS 5613 (Part-II/Sec-1) -1985 (Part-III/Sec.1) -1989 | Code of practice for design, installation and maintenance of overhead power lines | ANSI/ASCE 10-90(1991) |
| 36. | IS 5613 (Part-II/Sec-2) -1985 (Part-III/Sec.2) -1989 | Code of practice for design, installation and maintenance of overhead power lines (Section 2: Installation and maintenance) |  |
| 37. | IS 6610-1972 | Specification for heavy washers for steel structures. |  |
| 38. | IS 6639-1972 | Hexagonal bolts for steel structure. | ISO/R 272-1968 ASTM A394 CSA B33.4 |
| 39. | IS 6745-1972 | Methods for determination of weight of zinc coating of zinc coated iron and steel articles. | ASTM A90 ISO 1460 |
| 40. | IS 8263-1976 | Method of radio interference tests on high voltage insulator | IEC 437-1973 NEMA 107-1964 |
| 41. | IS 8269-1976 | Method of switching impulse tests on HV insulators. | IEC 506-1975 |
| 42. | IS 8500-1977 | Specification for weldable structural steel (medium and high strength qualities) | BSEN 10025 |
| 43. | IS 9708-1980 | Specification for Stock Bridge vibration dampers for overhead power lines. |  |
| 44. | IS 9997-1988 | Aluminium alloy redraw rods | IEC 104-1987 |
| 45. |  | Hard drawn aluminium wires for overhead line conductors. | IEC 889-1987 |
| 46. |  | Thermal mechanical performance tests and mechanical performance tests on string insulator units. | IEC 575-1977 |
| 47. |  | Salt fog pollution voltage withstand tests. | IEC 507-1991 |
| 48. |  | Residual strength of string insulator units of glass or ceramic material for overhead lines after mechanical damage of the dielectric. | IEC 797-1984 |
| 49. |  | Guide for the selection of insu- lators in respect of polluted conditions. | IEC 815-1986 |
| 50. |  | Tests on insulators of ceramic material or glass for overhead lines with a nominal voltage greater than 1000 Volts. Ozone test on elastomer | IEC 383-1993 (Part I and II ) |
| 51. |  |  | ASTM D-1171 |
| 52. | IS 1363 | Hexagonal head bolts, screws and nuts of product Grade - C |  |
|  | Part - 1 | Hexagonal head bolts | ISO 4016 |
|  | Part - 3 | Hexagonal nuts | ISO 4034 |
| 53. | IS 1367 | Technical supply conditions for threaded steel fasteners |  |
|  | Part III Part VI | Mechanical properties and test methods for bolts, screws and studs with full loadability Mechanical properties and test methos for nuts with full laodability | ISO 898-1 ISO/DIS 898/II |
| 54. |  | Indian Electricity Rules - 1956 |  |
| 55. |  | Indian Electricity Act - 1910 |  |
| 56. | IS 1498-1970 | Classification and identification of soil for general engineering purposes |  |
| 57. | IS 1888-1982 | Method of load test on soils |  |
| 58. | IS 1892-1979 | Code of practice for subsurface investigation for foundation |  |
| 59. | IS 2911-1979 (Part-I) | Code of practice for design and construction of pile foundations |  |
| 60. | IS 4453-1980 | Code of practice for exploration by pits, trenches, drifts and shafts |  |
| 61. | IS 6935-1973 | Method for determination of water level in a bore hole |  |
| 62. | IS 8009-1976 (Part-I) | Code of practice for calculation of settlement of foundation subjected to symmetrical vertical loads (Shallow Foundation) |  |
| 63. | IS 2386-1963 (Part-3) | Methods of test for aggregates for concrete : Specific gravity, density, voids, absorption and bulking |  |
| 64. 65. | IS 14000-1994 | Quality management and quality assurance standards GRIDCO Safety Manual (draft)-1997 | ISO 9000-1994 |
| 66. |  | Composite insulators for a.c. overhead lines with a nominal voltage greater than 1000 V : Definition, test methods and acceptance criteria | IEC 1109-1992 ANSI C29-11 IEEE 987 |