CHAPTER 38: SPECIFICATION FOR DESIGN AND FABRICATION OF TRANSMISSION LINE TOWERS

38.1.1.0	 SCOPE

38.1.1.1	This section covers the design, fabrication, galvanizing, supply and delivery, erection, testing and commissioning at site of galvanized steel structures, bolts & nuts, tower accessories etc. for transmission line towers covered under this Bid Document and as per Specification.

Single circuit stringing shall be made possible in the Double circuit towers for any voltage level.

38.1.2.0	 GENERAL DESCRIPTION OF THE TOWER

38.1.2.1	General

38.1.2.1.1 The towers shall be of self-supporting hot dip galvanized lattice steel type designed to carry the line conductors with necessary insulators, earth wires and all fittings under all loading conditions.

38.1.2.1.2 The tower shall be fully Galvanised using mild steel or / and high tensile steel sections. Bolts and nuts with spring washer are to be used for connections.

38.1.2.2	Type of Towers

38.1.2.2.1 Normal Towers

The towers for transmission lines are classified as given below. The bidder shall design and quote for the following four types of towers (Standard/Standard Towers):

Tower type D shall also be used as a Dead-End tower.

Type of	Deviation	Typical Use

Tower	Limit

| Type of | Deviation | Typical Use |
| --- | --- | --- |
| Tower | Limit |  |
| A | 0 – 2 deg. | To be used as tangent tower with single or Double suspension Insulator String |
| B | 2 - 15 deg. | a) Angle towers with Single / Double Tension insulator string. |
| C | 15 - 30 deg. | a) Angle tower with single or /and double tension insulator string. |
|  |  | b) Also to be used for locations where uplift exist. |
|  |  | c) Section tower for anti cascading condition. |
| D | 30 - 60 deg/ Dead End. | a) Angle tower with Single or / and Double tension insulator string. |
|  |  | b) Also to be used for locations where uplift exist. |
|  |  | c) Dead end with 0 deg. to 15 deg. deviation both on line side and sub station side (slack span) |

Dead End.	a) Angle tower with Single or / and Double tension insulator string.

b) Also, to be used for locations where uplift exist.

c) Dead end with 0 deg. to 15 deg. deviation both on line side and sub station side (slack span)

The angles of line deviation specified are for the design span. The span may however be increased up to an optimum limit with reduced angle of line deviation if adequate ground and phase clearances are available. For this purpose, the Contractor shall prepare a tower rating chart (weight/wind span as function of various angles of deviations).

38.1.2.2.2 Body Extensions Truncations & Unequal Leg Extensions Truncations

a) All Normal towers mentioned in Clause above shall be designed for 3, 6, 9, 12, 15- and 18-meter body extensions for maintaining adequate ground clearance as per the terrain, without reducing the safety margins available in normal towers in any manner. Towers which require more than 18 m extension shall be treated as Special Towers.

b) All above extensions to normal towers shall be treated as part of normal towers only.

c) Prices shall be quoted as per weight (in MT) basis on the guaranteed black weight of towers.

d) Designs and drawings of all type of towers with extensions as mentioned in (a) above along with foundations (all type) shall be submitted for approval of the employer irrespective of whether such requirements are there or not for a particular transmission line.

e) Attached as ANNEXURE: (Chapter: 34 (A))

38.1.2.2.3 Special Towers

The towers which will be specially designed for very long spans such as Major River crossings etc. that cannot be crossed by normal tower with extensions shall be special towers.

The Bidder must furnish design of each of these special towers for approval of the Employer. The Contractor shall quote for these towers separately at unit rates by weight per MT of super structure and fittings and will supply the same if so required.

38.1.3.0	 SPANS AND CLEARANCES

38.1.3.1	Normal span, Wind Span & Weight Span

The normal ruling span, wind span and weight span to be adopted for lines covered under this Specification are specified in Annexure-1 of this section along with all other parameters.

38.1.3.2	Electrical Clearances

38.1.3.2.1 Ground Clearance

a) The minimum ground clearance of conductors above ground shall not be less than the limits specified in Line Data at Annexure I, at a conductor temperature of 95°C (for AAAC conductors) and 85°C (for ACSR conductors) and in still air. However, to achieve the above clearance the standard tower heights include the following additional allowances:

b) 150 mm sag errors in stringing;

c) Conductor creep as calculated by over tensioning the conductor at a temperature of 30°C lower than the stringing temperature or as determined from the sag-tension tables, which include the final sags including the effects of creep.

38.1.3.2.2 Clearances of live parts form cross arm & towers

The minimum clearances shall be adopted from the following Table.

| SL No | Item | Swinging in degrees | Minimum electrical clearances for line voltage 132 kV | Minimum electrical clearances for line voltage 220 kV | Minimum electrical clearances for line voltage 400 kV |
| --- | --- | --- | --- | --- | --- |
| 1 | SUSPENSION STRINGS |  |  |  |  |
|  | (a) Single suspension string | Nil | 1530 | 2130 | 3050 |
|  |  | 15° | 1530 | 1980 | 3050 |
|  | (in mm) | 30° | 1370 | 1830 | 1860 |
|  |  | 45° | 1220 | 1675 | - |
|  |  | 60° | 1070 | - | - |
|  | (b) Double suspension (c ) Pilot Insualtor | Nil 15° | 1530 | 2130 | 3050 3050 |
| 2 | Tension string | Nil | 1530 | 2130 | 3050 |
|  | Single/ Double |  |  |  |  |
| 3 | Jumper | Nil | 1530 | 2130 | 3050 |
|  |  | 10° | 1530 | 2130 | 3050 |
|  |  | 20° | 1070 | 1675 | 1860 |
|  |  | 30° | 1070 | 1675 | - |
| 4 | Min vertical distance between conductor or X-arm (single/double circuit) (in mm) |  | 3900 | 4900 | 8000 |
| 5 | Min horizontal distance between conductors (single/ double circuit)(in mm) |  | 6800 | 8400 | 15000 |
| 6 | Mid span clearance (in mm) |  | 6100 | 8500 | 9000 |
| 7 | Ground Clearance (in mts) |  | 6.1 | 7.015 | 8.84 |

38.1.3.2.3 Railway Crossings, etc

For railway crossing the clearances from the lowest conductor points to the rail level shall not be less than what is required to comply in all respects with the "Regulation governing the placing of transmission lines across railway tracks" issued by the railway board. In case of trunk road crossings, the clearance from the lowest conductor point to road level shall not contravene the provision of IE rules. Power and Tele-communication line crossings are to be constructed strictly in accordance with provision of IE Rules.

38.1.4.0	 DESIGN DRAWINGS

38.1.4.1	The relevant drawings for all the towers and their extension shall be furnished by the Contractor to the Employer which shall include structural/erection drawings, shop fabrication drawings, Bill of Materials, foundation working drawings.

38.1.4.2	The structural/erection drawings, Bill of materials and shop fabrication drawings for all the towers and their extensions shall be submitted as specified in this Bid document. Documents shall be submitted in four copies and will be finally approved by the Employer. The mass/fabrication shall be taken up from the approved shop drawings. The overall responsibility of fabricating tower members correctly lies with the Contractor only and the Contractor shall ensure that all the tower members can be fitted while erecting without any undue strain on them.

38.1.4.3	The tower accessories drawings like name plate, danger plate, phase plate, anti climbing device, step bolt, D-shackle etc. shall also be prepared by the Contractor and shall be submitted to the Employer, in three copies, along with one reproducible, for record. These drawings shall be prepared in A4 size only.

38.1.4.4	All the drawings shall 'have a proper name plate clearly displaying the name of “Assam Electricity Grid Corporation Ltd ” on right hand bottom corner. The exact format of the nameplate shall be handed over to the successful bidder for incorporation of the same on all the drawings. Also, all the drawings shall carry the following statement and shall be displayed conspicuously on the drawing: WARNING: THIS IS PROPRIETARY ITEM AND DESIGN RIGHT IS STRICTLY RESERVED WITH AEGCL. UNDER NO CIRCUMSTANCES THIS DRAWING SHALL BE USED BY ANYBODY WITHOUT PRIOR PERMISSION FROM THE EMPLOYER IN WRITING.

38.1.4.5	While submitting the structural drawings, bill of materials and any other drawings pertaining to the subject transmission line, the Contractor shall clearly indicate on each drawing Bid Reference No., Name of the transmission line and project, letter reference no. and date on which the submission are made. The same practice is also to be followed while submitting distribution copies. The Contractor shall be required to submit 15 copies of all relevant drawings for necessary distribution.

38.1.5.0	 SLENDERNESS RATIO

38.1.5.1	Slenderness ratio for members shall be computed in accordance with Clause 10 of IS: 802. The limiting values of L/R shall be as follows:

(a) Leg members, G.W. peak and cross arm lower member: 		150

(b) Bracings:								150

(c) Redundant members and those carrying nominal stress:		250

(d) Tension member:							400

38.1.6.0	 CONDUCTOR CONFIGURATION

38.1.6.1	In case of the double circuit line, the six power conductors shall be square type of formation. For, single circuit stringing on D/C towers, the three power conductors shall be in vertical line formation on one side, at distances suiting to the specified clearance requirements. Earth wire/OPGW shall be provided above the conductors at suitable distance to offer effective shielding and safe clearance.

38.1.7.0	 HEIGHT AND LOCATION OF GROUND WIRES

38.1.7.1  Provision of single earth wire / ground wire shall be made in the design of the towers. The height and location of the ground wires will be such that the shield angle is not greater than 30 degrees and 20 degrees for 132KV/ 220 KV and 400 KV respectively (twin peak).

38.1.7.2	  The mid-span clearance between the earth wire and conductors shall be kept more than the clearance at the tower. The Contractor shall maintain the sag of the ground wire at least 10 percent less than that of the power conductor under all temperature conditions in still wind at the normal spans so as to give a mid span separation greater than that at the supports.

38.1.8.0	 LOADS ON TOWERS

38.1.8.1	 The tower members shall be designed for three conditions of loadings. The conditions with their combinations of loadings are as follows:

A) Reliability Condition (Normal Condition)

i)	Transverse Loads as per as per IS-802-2015, Part 1, sec 1

ii)	Vertical Loads as per per IS-802-2015, Part 1, sec 1

iii)	Longitudinal Loads as per IS-802-2015, Part 1, sec 1

B) Security Condition (Broken wire condition)

i)	Transverse Loads as per IS-802-2015, Part 1, sec 1

ii)	Vertical Loads as per IS-802-2015, Part 1, sec 1

iii)	Longitudinal Loads as per IS-802-2015, Part 1, sec 1

C) Safety Condition (Construction and Maintenance)

a) Normal Condition

i)	Transverse Loads as per IS-802-2015, Part 1, sec 1

ii)	Vertical Loads as per IS-802-2015, Part 1, sec 1

iii)	Longitudinal Loads as per IS-802-2015, Part 1, sec 1

b) Broken Wire Condition

i)	Transverse Loads as per IS-802-2015, Part 1, sec 1

ii)	Vertical Loads as per IS-802-2015, Part 1, sec 1

iii)	Longitudinal Loads as per IS-802-2015, Part 1, sec 1

38.1.8.2	 Transverse Loads: Reliability Condition (Normal Condition)

Under these following loads shall be taken into account:

a) Wind Load on Conductor and Ground Wire:

This shall be calculated by taking the basic wind pressure be acting normal to the line.

b) Wind Load on Insulator String:

Wind load on insulator strings shall be determined from the attachment point to the centre line of the conductor in case of suspension towers and up to the end of clamp in case of tension towers. The Design wind pressure shall be considered acting on 50% area of insulator string projected on a plan, which is parallel to the longitudinal axis of the string.

c) Wind Load on Towers:

This shall be calculated considering the wind to be acting normally on face of the tower.

d) Transverses Loads from Mechanical Tension of Conductors and Ground Wire (Due to line deviation):

This is the component of conductor/ground wire tension at tower acting in the transverse direction of the line. In calculating this force; the conductor/ground wire tension is either the tension at every day temperature (32˚C) &100% of full wind pressure or the tension at minimum temperature and 36% of full wind pressure whichever is more.

38.1.8.3	 Transverse Loads: security condition

a) Suspension Towers

i. Transverse loads due to wind acting on tower structure, conductors, ground wires and insulators shall be taken as nil.

ii. Transverse loads due to line deviation shall be based on component of mechanical tension of conductors and ground wires corresponding to everyday temperature and nil wind condition. For broken wire the component shall be corresponding to 75% of mechanical tension of conductor and 100% of mechanical tension of ground wire at every day temperature and nil wind.

b) Tension and Dead-End Towers

i. Transverse loads due to wind action on tower structure, conductors, ground wire and insulators shall be as per Clause: 38.1.8.2 (a) and (b) 60% wind span shall be considered for broken wire and 100% for intact wires.

ii. Transverse loads due to line deviation shall be the component of 100% mechanical tension of conductor and ground wire as defined in Clause: 38.1.8.2 (d).

38.1.8.4	 Transverse Loads: safety condition

a) Normal Condition: -- Suspension, Tension and dead-End Tower

i) Transverse loads due to wind action on tower structure, conductors ground wires and insulators shall be taken as nil.

ii) Transverse loads due to mechanical tension of conductor or ground wire shall be calculated in same manner as in Clause: 38.1.8.2 (d) but with tension corresponding to everyday temperature and nil wind.

b) Broken Wire Condition: -- Suspension, Tension and dead-End Tower

i) Transverse loads due to wind action on tower structure, conductors, ground wire, insulators shall be taken as nil.

ii) Transverse load due to mechanical tension of conductor or ground wire on account of line deviation shall be taken as follows:

TM =	TI x sin φ/2, where,

Where, 	TM =	Load

TI =	50% of tension of conductor and 100% of tension of ground wire at everyday temperature and nil wind for suspension tower and 100% for angle and dead-end towers for both conductor and ground wire.]

Φ =	Angle of deviation of tower.

38.1.8.5	 Vertical Loads: Reliability Condition (normal condition)

i) Loads due to weight of each conductor and ground based on appropriate weight span, weight of insulator strings and accessories.

ii) Self weight of structures up to tower panel under consideration.

38.1.8.6	Vertical Loads: Security Condition

i) Loads due to weight of each conductor or ground wire based on appropriate weight span, weight of insulator strings and accessories taking broken wire condition where the load due to weight of broken conductor/ground wire shall be considered as 60% of weight span. For intact wire the vertical load shall be considered as given in Clause: 38.1.8.5.

ii) Self weight of structures up to tower panel under consideration.

38.1.8.7	 Vertical Loads: Safety Condition

(i) Same as Clause 38.1.8.6 (i) multiplied by overload factor of 2.0

(ii) Same as Clause 38.1.8.6 (ii).

(iii) A load of 1500 N shall be considered acting at each cross-arm tip as a provision for weight of line man with tools.

(iv) An additional load of 3500 N at cross arm tip.

(v) All bracings and redundant members of the towers which are horizontal or inclined up to 150 from horizontal shall be designed to withstand as ultimate vertical load of 1500 N considered as acting at centre, independent of all other loads.

38.1.8.8 Longitudinal Loads: Reliability Condition

A) Suspension and Tension Towers

i) Longitudinal loads for Suspension and Tension towers shall be taken as nil.

ii) Longitudinal loads which might be caused on tension towers by adjacent spans of unequal length shall be neglected.

B) Dead End Tower

i) Longitudinal loads for Dead End Towers shall be considered corresponding to mechanical tension of conductors and ground wires at every day temperature & design wind pressure or at minimum temperature with 36% of design wind pressure, whichever is more stringent.

38.1.8.9	 Longitudinal Loads: Security Condition

A) Suspension Towers

The longitudinal loads corresponding to 50% of the mechanical tension of conductor and 100% of mechanical tension of ground wire shall be considered under everyday temperature and no wind pressure for broken wire only.

B) Tension Towers

Horizontal loads in longitudinal direction due to mechanical tension of conductors and ground wire shall be taken for loading criteria mentioned in Clause: 38.1.8.8 (B) for broken wires. For intact wires these loads shall be considered nil.

C) Dead End Towers

Horizontal loads in longitudinal direction due to mechanical tension of conductors and ground wire shall be taken for loading criteria mentioned in Clause: 38.1.8.8 (B) for intact wires; however, for broken wires these loads shall be considered nil.

38.1.8.10 Longitudinal Loads: Safety Condition

A) Normal Condition

i) Suspension and Tension Towers

These shall be taken as nil.

ii) Dead End Towers

These loads for Dead End towers shall be considered as corresponding to mechanical tension of conductors/ground wire at every day temperature and nil wind. Longitudinal loads due to unequal spans may be neglected.

B) Broken wire Condition

i) Longitudinal loads during construction simulating broken wire condition will be based on stringing of one earth wire or one complete phase conductor at one time.

ii) Suspension Towers

Longitudinal loads during stringing on suspension towers should be normally imposed only by the passing restriction imposed during pushing of the running block through the sheave. It will apply only on one complete phase of sub-conductor or one earth wire. It will be taken as 10000 N per sub-conductor or 5000 N per earth wire.

iii) Tension and Dead-End Tower

Angle Towers used as dead end during stringing simulating broken wire condition shall be capable of resisting longitudinal loads resulting from load equal to twice the sagging tension (sagging tension is 50% of the tension at every day temperature and nil wind) for one earth wire or one complete phase sub- conductors which is in process of stringing. At other earth wire or conductor attachment points for which stringing has been completed, loads equal to 1.5 times the sagging tension will be considered.

38.1.8.11 Anti Cascading Checks

i) All angle towers shall be checked for the following anti-cascading conditions with all conductors and G.W. intact only on one side of the tower.

ii) Transverse Loads:- These loads shall be taken under no wind condition.

iii) Vertical Loads:- These loads shall; be the weight of conductor/ground wire intact on one side of tower, weight of insulator strings and accessories.

iv) Longitudinal Loads:- These Loads shall be the pull of conductor/ground wire at every day temperature and no wind applied simultaneously at all points on one side with zero-degree line deviation.

38.1.8.12 BROKEN WIRE CONDITIONS

A) SINGLE CIRCUIT TOWERS

Any one-phase conductor or earth wire broken, whichever is more stringent for a particular member.

B) DOUBLE CIRCUIT TOWERS

i) SUSPENSION TOWERS

Any one phase conductor or earth wire broken, whichever is more stringent for a particular member.

- ANGLE TOWERS, TYPE-B & C

Any two phases broken on the same side and same span or any one phase and one ground wire broken on the same side and same span whichever combination is more stringent for a particular member.

- ANGLE TOWERS, TYPE-D (Dead End Tower)

Any three phases broken on the same side and same span or any two phases and one ground wire broke on the same side and same span whichever combination is more stringent for a particular member.

38.1.9.0	 DESIGN WIND PRESSURE

38.1.9.1 	Design Wind Pressure for the purpose of this Specification shall be taken as 793 N/m2 which corresponds to wind velocity at 10 m height. For Design Wind Pressure at other heights reference shall be made to IS: 802 or ‘Transmission Line Manual’ published by Central Board of Irrigation and Power, New Delhi. The Design Wind Pressure mentioned above is corresponds to Wind Zone-5, Reliability Level-1 and Terrain Category-2 as per IS: 802.

38.1.10.0 OTHER DESIGN PARAMETERS

38.1.10.1 For other design parameters to be adopted for the design of towers reference shall be made to Annexure I of this Specification.

38.1.11.0 MATERIALS

38.1.11.1 Tower Steel Sections

38.1.11.1.1	 IS Steel Sections of tested quality of conformity with IS:2062 (Designated Y.S. 250 MPa) or/and IS:8500 (Designated Y.S. 350 Mpa) are to be used in towers, extensions and stub setting templates. The Contractor can use other equivalent grade of structural steel angle sections and plates conforming to International Standards (IS-802(2015/P1 to 3) - 	Code of practice for use of structural steel in overhead transmission line towers). However, use of steel grade having designated yield strength more than that of EN 10025/BS-4360-50B grade (355MPa) is not permissible.

38.1.11.1.2 Steel plates below 6mm size exclusively used for packing plates/packing washers produced as per IS: 1079 (Grade -0) are also acceptable. However, if below 6mm size plate are used as load bearing plates viz gusset plates, joint splices etc. the same shall conform to IS: 2062 / BS : 4360 or equivalent standard meeting mechanical strength/metallurgical properties corresponding to Fe-410 or above grade (designated yield strength not more than 355MPa), depending upon the type of grade incorporated into design. The chequered plates shall conform to IS: 3502.

38.1.11.1.3 For designing of towers, preferably rationalized steel sections have been used. During execution of the project, if any particular section is not available, the same shall be substituted by higher section at no extra cost to Employer and the same shall be borne by the Contractor. However, design approval for such substitution shall be obtained from the Employer before any substitution.

38.1.11.2 Fasteners: Bolts, Nuts and Washers

38.1.11.2.1 All bolts and nuts shall conform to 18-12427. All bolts and nuts shall be galvanized as per IS: 1367 (Part-13)/18:2629 and shall have hexagonal head and nuts, the heads being forged out of the solid truly concentric, and square with the shank, which must be perfectly straight.

38.1.11.2.2 The bolt shall be of 16/24 mm diameter and of property class 5.6 as specified in IS: 1367 (Part-III) and matching nut of property class 5.0 as specified in IS: 136: (Part-VI).

38.1.11.2.3 Bolts up to M 16 and having length up to 10 times the diameter if the bolt should be manufactured by cold forging and thread rolling process to obtain good and reliable mechanical properties and effective dimensional control. The shear strength of bolts for 5.6 grade should be 31 0 MPa minimum as per IS: 12427. Bolts should be provided with washer face in accordance with 18:1363 (Part-I) to ensure proper bearing.

38.1.11.2.4 Nuts should be double chamfered as per the requirement of IS: 1363 Part-II'. It should be ensured by the manufacturer that nuts should not be overlapped beyond 0.4MM oversize on effective diameter for size up to M 16.

38.1.11.2.5 Fully threaded bolts shall not be used. The length of bolts shall be such that the threaded portion will not extend into the place of contact of the members.

38.1.11.2.6 All bolts shall be threaded to take the full depth of the nuts and threaded for enough to permit firm gripping of the members, but not further. It shall be ensured that the threaded portion of each bolt protrudes not less than 3 mm and not more than 8mm when fully tightened. All nuts shall fit tight to the point where the shank of the bolt connects to the head.

38.1.11.2.7 Flat and tapered washers shall be provided wherever necessary. Spring washers shall be provided for insertion under all nuts. These washers shall be steel electrogalvanised, positive lock type and 3.5mm in thickness for 16mm dia bolt and 4.5mm for 24mm bolt.

38.1.11.2.8 To avoid bending stress in bolts or to reduce it to minimum, no bolt shall connect aggregate thickness of members more than three (3) times its diameter.

38.1.11.2.9 The bolt positions in assembled towers shall be as per structural drawing.

38.1.11.2.10 Bolts at the joints shall be so staggered that nuts shall be tightened with spanners without fouling.

38.1.11.2.11 To ensure effective in-process Quality control it is essential that the manufacturer should have in house testing facility for all tests like weight of zinc coating, shear strength and other tests etc. The manufacturer should also have proper Quality Assurance System which should be in line with the requirement of this 5pecification and IS: 14000 series Quality System Standard

38.1.12.0 TOWER ACCESSORIES

38.1.12.1 Arrangement shall be provided for fixing of all tower accessories to the tower at a height between 2.5 meters and 3.5 meters above the ground level.

38.1.12.2 Step Bolts & Ladders

38.1.12.2.1 Each tower shall be provided with step bolts conforming to IS: 10238 of not less than 16mm diameter and 175mm long spaced not more than 450mm apart and extending from 2.5 meters above the ground level to the top of the tower. The step bolt shall be fixed-on one leg up to waist level and on two diagonally opposite legs above waist level up to top of the towers. Each step bolt shall be provided with two nuts on one end to fasten the bolt securely to the tower and button head at the other end to prevent the feet from slipping away. The step bolts shall be capable of with standing a vertical load not less than 1.5 KN.

38.1.12.2.2 For special towers, where the height of the super structure exceeds 50 meters, ladders along with protection rings as per approved design shall be provided in continuation of the step bolts on one face of the tower from 30 meters above ground level to the top of the special structure. From 2.5m to 30m height of super structure step bolts shall be provided. Suitable platform using 6mmthick perforated chequered plates along with suitable railing for access from step bolts to the ladder and from the ladder to each cross-arm tip and the ground wire support shall also to be provided. The platform shall be fixed on tower by using counter-sunk bolts.

38.1.12.3 Insulator Strings and Earth wire Clamps Attachments

38.1.12.3.1 Single / Double suspension insulator string assemblies shall be used for ‘A’ type tower as required. For the attachment of Suspension Insulator string, a suitable strain plate of sufficient thickness for transferring the load to the tower body shall be provided. To achieve requisite clearances, if the design calls for providing extra D-shackles, link plate etc. before connecting the 1nsulator string the insulator string the same shall be supplied by the Contractor.

38.1.12.3.2 At tension towers strain plates of suitable dimensions placed on the underside of each cross-arm tip, shall be provided for taking the hooks or D-shackles of the tension insulator strings. Full details of the attachments shall be provided to the successful bidder. To achieve requisite clearances, if the design calls for providing extra D-shackles, link plate etc. before connecting the insulator string the same shall be supplied by the Contractor.

38.1.12.3.3 All important crossing like Railway Tracks, Important Roads, Rivers or any other Crossings of similar nature shall be done with Double Insulator String.

38.1.12.4 Earth wire Clamps Attachment

38.1.12.4.1 Suspension Clamp

The detailed drawing shall be submitted by the Contractor for Employer's approval. The Contractor shall also supply U- bolts, D-shackles wherever required.

38.1.12.4.2 Tension Clamps

Earth wire peaks of tension towers shall be provided with suitable plates to accommodate the shackle of tension clamps. The contractor shall also supply the U-bolts wherever required and take Employer's approval for details of the attachments before the mass fabrication.

38.1.12.5 Anti-climbing Device

Barbed wire type anti climbing device, as per IS 5613 shall be provided and installed by the Contractor for all towers. The barbed wire shall conform to IS-278 (size designation A 1). The barbed wires shall be given chromatin dip as per procedure laid down in IS: 160.

38.1.12.6 Danger, Number and Phase plate

Danger Plates, Number plates and phase plates shall be provided and installed by the Contractor.

a) Each tower shall be fitted with a danger plate, number plate and a set of phase plates. The transposition tower should have the provision of fixing phase plates on both the transverse phases.

b) The letters, figures and the conventional skull and bones of danger plates shall conform to IS-2551 and shall be in a signal red on the front of the plate.

c) The corners of the danger, number and circuit plates shall be rounded off to remove sharp edges.

d) The letters of number and circuit plates shall be red enameled with white enameled background.

38.1.12.7 Aviation Requirements

Aviation requirements, if indicated separately in Schedule of Requirements shall be in the scope of the Contractor and the same shall conform to IS: 5613.

38.1.13.0 TOWER FABRICATION

38.1.13.1 The fabrication of towers shall be in conformity with the following:

38.1.13.1.1 Except where hereinafter modified, details of fabrication shall conform to IS: 802 (Part-II) or the relevant international standards.

38.1.13.1.2 The tower structures shall be accurately fabricated to connect together easily at site without any undue strain on the bolts.

38.1.13.1.3 No angle member shall have the two leg flanges brought together by closing the angle.

38.1.13.1.4 The diameter of the hole shall be equal to the diameter of bolt plus 1.5mm.

38.1.13.1.5 The structure shall be designed so that all parts shall be accessible for inspection and cleaning. Drain holes shall be provided at all points where pockets of depression are likely to hold water.

38.1.13.1.6 All identical parts shall be made strictly inter-changeable. All steel sections before any work are done on them shall be carefully levelled, straightened and made true to detailed drawings by methods which will not injure the materials so that when assembled, the adjacent matching surfaces are in close contact throughout. No rough edges shall be permitted in the entire structure.

38.1.13.1.7 Minimum Thickness of Tower Members:

The minimum thickness of galvanised and painted tower members shall be as follows: -

| ITEM | Minimum thickness in mm |  |
| --- | --- | --- |
|  | Galvanised | Painted |
| Leg members & lower members of cross arms in compression | 5 | 6 |
| Other members | 5 | 5 |

38.1.13.1.8 No tower angle member shall be less than 45x45x5 mm

38.1.13.2 Drilling and Punching

38.1.13.2.1 Before any cutting work is started, all steel sections shall be carefully strengthened and trued by pressure and not by hammering. They shall again be trued after being punched and drilled.

38.1.13.2.2 Holes for bolts shall be' drilled or punched with a jig but drilled holes shall he preferred. The punching may be adopted for thickness up to 16mm. Tolerances regarding punch holes are as follows:

a) Holes must be perfectly circular and no tolerances in this respect are permissible.

b) The maximum allowable difference in diameter of the holes on the two sides of plates or angle is 0.8mm. i.e. the allowable taper in a punched hole should not exceed 0.8 mm on diameter.

c) Holes must be square with the plates or angles and have their walls parallel.

38.1.13.2.3 All burrs left by drills or punch shall be removed completely. When the tower members are in position the holes shall be truly opposite to each other. Drilling or reaming to enlarge holes shall not be permitted.

38.1.13.3 Erection mark

38.1.13.3.1	Each individual member shall have erection mark conforming to the component number given to it in the fabrication drawings. The mark shall be marked with marking dies of 16mm size before galvanizing and shall be legible after galvanizing,

38.1.13.3.2 Erection Mark shall be A-BB-CC-DDD

A	=	Employer's code assigned to the Contractors -Alphabet

BB	=	Contractor's Mark-Numerical

CC =	Tower Type Alphabet.

DDD=	Number mark tube assigned by Contractor -Numerical.

38.1.14.0 QUANTITIES AND WEIGHTS

38.1.14.1 The quantities of the following items have been envisaged in Metric Tone (MT) in the relevant price Schedules for various types of towers:

i)	            Basic Body.

ii)	Body Extensions.

iii)	Stubs & Cleats

iv)	Bolts & Nuts including spring washers and step bolts etc.

During detail engineering, proto assembly of each of the above items shall be inspected, Tested and approved by AEGCL and subsequently shall be released for fabrication and manufacturing as per the Technical Specification by the Contractor.

38.1.15.0 WEIGHTS OF TOWER

38.1.15.1 The Bidder shall furnish the guaranteed weights of each type of tower and stubs. The weight of tower shall mean the weight of tower, calculated by using the standard sectional weights of all steel members of the sizes indicated in the approved fabrication drawings and bill of materials without taking into consideration the reduction in weight due to drilling of bolt holes, skew cuts, chamfering etc. or increase in weight due to galvanizing but taking into considering the weight of the special fillings, bolts, nuts, washers etc.

38.1.15.2 After award of the contract, the bidder shall submit to the Employer for its approval, detailed design calculations and drawings for each type of tower. In case, the weight of the tower, finally approved and accepted by the Employer on the basis of the designs and drawings so submitted is more than the guaranteed weight, no extra amount shall be paid to the contractor.

38.1.15.3 If, however, the weight of the finally approved and adopted tower is less than the guaranteed weight, the payment shall be made on the basis of the finally accepted weights only.

38.1.15.4The contractor, while designing towers, shall use only such sizes of steel structures, which are easily procurable. If for any reason, the sections approved are not easily procurable, it is the responsibility of the contractor to procure the alternative sizes, which are satisfactory from the point of view of design, fabrication, galvanising and supply the same at no additional cost. The finally accepted weight shall mean the weight of each type of tower, design of which has been accepted.

38.1.16.0 STUB TEMPLATE

38.1.16.1 Stub templates shall be designed, and the Bidder shall quote unit rate for each type of tower. These stub templates shall be painted with two coats of red-oxide zinc chromate primer as per relevant IS.

38.1.17.0 GALVANIZING AND PAINTING

38.1.17.1 Galvanizing and painting of the various members of the structures shall be done only after all works of sawing, shearing, drilling, filing, bending and matching are completed. Galvanizing shall be done by the hot dip process as recommended in IS: 2629 or other such authoritative international standards and shall produce a smooth, clean and uniform coating of not less than 900 gm per square meter (130 microns). The preparation for galvanizing and the galvanizing process itself must not affect adversely the mechanical properties of the treated materials.

38.1.17.2 All assembly bolts shall be thoroughly hot dip galvanized after threading. Threads shall be of a depth sufficient to allow for the galvanized coating, which must not be excessive at the root of the threads, so that the nut shall turn easily on the completed bolts without excessive looseness. The nut threads shall not be galvanized, but oiled only.

38.1.17.3 The outside surface shall be galvanised. Sample of galvanised materials shall be supplied to the galvanising test set out in IS 729 or other such authoritative international standards.

38.1.17.4 The portion of the stub angle from 150 mm below the plinth level shall be black and the remaining portion shall be galvanised.

38.1.17.5 The parts, which are to be painted, shall be thoroughly cleaned. Two coats of a good quality primer shall be applied to produce a smooth void less surface before applying one coat of approved quality aluminium paint at works. The final coating of aluminium paint shall be applied after erection at site.

38.1.18.0 EARTHING

38.1.18.1 To keep provision in the towers for earthing, two holes of 17.5 mm diameter and about 50 mm apart shall be drilled on each of the legs of the towers, such that the lower hole is about 350 mm above the ground level, clear of the concrete muffing, for connecting the earthing strip.

38.1.19.0 TEST AND TEST CERTIFICATE

38.1.19.1 Each consignment ready for transportation shall be offered to the Employer for inspection before dispatch. Samples of fabricated tower materials shall be subjected to following tests: -

a. Tower steel: The structural steel shall conform to IS 226 and IS 8500, BS 4360-1068 or ISO / R 630 other such authoritative international standards. Manufacturer's test certificate shall be submitted for all used steel.

b. Galvanising: The galvanizing shall be as per IS 2633 or BS 729 other such authoritative international standards. Zinc coating over the galvanized surfaces shall not be less than 900 gm per square meter (130 microns).

c. Bolts and nuts: Manufacturer's test certificate as per standard practice shall be submitted.

38.1.19.2 Test at Contractor's Premise:

The contractor shall fabricate one specimen tower of each type as soon as possible after placement of order and before starting the bulk fabrication of the towers ordered. It shall be assembled on a foundation as nearly similar as practicable to site and tested with suitable test loads as per specified broken wire condition, multiplied by the corresponding factor of safety to ensure that the design and fabrication complies with the requirements. Each structure shall be capable of withstanding the above-mentioned tests without any injury or any permanent deflection at any part. If any member is found to be weak or damaged the design should be suitably modified and the tower re-tested.

After manufacture of first lot, finished members forming each type of towers shall be selected at random and tested for quality. The tower then shall be set on foundation as nearly similar as practicable to site and tested with equivalent test load for which the tower has been designed.

No tower or any member thereof, which failed under the test shall be supplied. No tests need to be carried out on the special towers and the 3 meter and 6 meter extensions. As such, they shall be very carefully designed on the basis of the results of the other types of towers.

If desired by the Employer, destruction test on towers shall be conducted. The Employer reserves the right to witness any and all of the tests carried out as above and so should be given 30 days advance notice of the dates on which such tests are scheduled to be carried out.

38.1.20.0 LIST OF STANDARDS AND GUIDES

List of Indian Standards and other related Publications

| Sl. No | Indian Standards | Title |
| --- | --- | --- |
| 1 | IS: 209-1992 | Specification for Zinc |
| 2 | IS 278-1991 | Galvanised Steel Barbed wire |
| 3 | IS 800-1991 | Code of Practice for Steel in General Building Construction. |
| 4 | IS: 802 - 2015 (Part1, 2,3) | Code of Practice for use of Steel in Overhead Transmission Line |
| 5 | IS: 808-1991 | Dimensions for Hot Rolled |
| 6 | IS: 875-1992 | Coe of Practice for Design Loads (other than Earthquakes) for Buildings and Structures |
| 7 | IS: 1363-1990 | Coe of Practice for Design Loads (other than Earthquakes) for Buildings and Structures |
| 8 | IS: 1367-1992 | Technical Supply Conditions for Threaded Steel/ Fasteners |
| 9 | IS: 1477-1990 | Code of practice for Painting of Ferrous Metals in Buildings |
| 10 | IS: 1573-199 | Electro-Plated Coatings of zinc on iron and Steel |
| 11 | IS: 1852-1993 | Rolling and Cutting Tolerances of Hot Rolled Steel Products |
| 12 | IS-1893-1991 | Criteria for Earthquake Resistant Design of Structures |
| 13 | IS: 2016-1992 | Plain Washers ISO/R887 |
| 14 | IS:2062-1992 | Steel for general structural purposes |
| 15 | IS: 2074-1992 | Ready Mixed Paint. Air Drying Red Oxide, Zinc Chrome, Red Oxide, Zinc Chrome Priming Specification |
| 16 | IS:2551-1990 | Danger Notice Plates |
| 17 | IS: 2629-1990 | Recommended Practice for Hot Dip Galvanizing of iron and steel |
| 18 | IS: 2633-1992 | Method of Testing Uniformity of Coating of Zinc Coated Articles |
| 19 | IS: 3043-1991 | Code of Practice for Earthing |
| 20 | IS: 3063-1994 | Single coil Rectangular section Spring Washers for Bolts, Nuts Screws |
| 21 | IS:3757-1992 | High Strength Structural Bolts |
| 22 | IS: 4759-1990 | Specification for Hot zinc coatings on structural steel and other Allied products |
| 23 | IS: 5369-1991 | General Requirements for Plain Washers |
| 24 | IS:5613-1993 | Code of Practice for Design installation and Maintenance of overhead Power Lines |
| 25 | IS:6610-1991 | Specification for Heavy Washers for Steel structures |
| 26 | IS: 6623-1992 | High Strength Structural Nuts |
| 27 | IS: 6639-1990 | Hexagon Bolts for Steel Structure |
| 28 | IS: 6745-1990 | Method for Determination of weight of Zinc coated iron and Steel Articles |
| 29 | IS: 8500-1992 | Specification for Wieldable Structural Steel (Medium & High Strength Qualities) |
| 29 | IS: 10238-1989 | Step Bolts for Steel Structures |
| 30 | IS: 12427-1988 | Bolts for transmission Line Towers |
| 31 |  | Indian Electricity Rules |
| 32 | Publication No.19 (N)700 | Regulation for Electrical Crossing of Railway Tracks |
| 33 | CBIP Publication No- | Transmission Line Manual |

Annexure I

1.1.1	Basic System Data for Transmission Lines

| SL. No | Description | 132 KV | 220 KV | 400 KV |
| --- | --- | --- | --- | --- |
| I | II | III | IV | V |
|  | Nominal system voltage KV rms | 132 | 220 | 400 |
|  | Highest system voltage KV rms | 145 | 245 | 420 |
|  | System of grounding | Solidly Grounded | Solidly Grounded | Solidly Grounded |
|  | Impulse insulation level KV peak | 650 | 1050 | 1425 |
|  | Power frequency withstand (wet) KV rms | 260 | 460 | 650 |
|  | Protective shielding angle against direct lightning | NOT EXCEEDING 300 | NOT EXCEEDING 300 | NOT EXCEEDING 200 |
|  | Creepage Distance | 27 mm/ KV | 27 mm/ KV | 27 mm/ KV |
|  | Minimum Corona extinction voltage at 50Hz AC system Dry condition (phase to earth) | Not less than 154 kV | Not less than 156 kV | Not less than 320 kV |
|  | Accessories for conductor and Earth wire | - Preformed armour rods - Mid-Span compression joints - Repair sleeves - Flexible copper bonds - Vibration dampers - Suspension clamps for earth wire - Tension clamp for earth wire |  |  |
|  | Insulator String Hardware | - Anchor shackle - Chain link - Yoke plate - Ball clevis - Arcing horn holding plate - Socket clevis - Arcing horns - Clevis eye - Free centre type/armour grip suspension clamp for suspension strings - Compression type dead end clamp - Balancing weight |  |  |

1.1.2	Basic Design Parameters for 132KV TL

| Item | Particulars | 132 kV Line (Single/double- 3phase) with AAAC |  |
| --- | --- | --- | --- |
| 1. SPAN | (i) Normal span (Design Span) | 335 M |  |
|  | (ii) Wind span | 335 M |  |
|  | (iii) Weight span, both span (total) - Maximum - Minimum | Suspension | Tension |
|  |  | 505 M 185 M | 505 M 0 M |
|  | (iv) Weight span, one span - Maximum - Minimum | Suspension | Tension |
|  |  | 315 M 100 M | 315 M -200 M |
| 2.Temparature Range |  | Conductor | Earth Wire |
|  | (I) Maximum | 850C | 530C |
|  | (ii) Minimum | 00C | 00C |
|  | (iii) Every Day | 320C | 320C |
| 3. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 4. Conductor | - Material | AAAC Panther |  |
|  | - Number of strands & size | 37/3.15 mm |  |
|  | - No. of conductor per phase | 1 |  |
| 5.Ground Wire | - Type | OPGW |  |
|  | - Size | 7 / 3.15 mm |  |
|  | - No. of earth wire | 1 |  |
| 6. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 7. Wind pressure | Maximum wind pressure up to a height of 10 M about mean retarding force | 793 N/m2 |  |
| 8.Ground Clearance (Under maximum sag) | (i) Rough country | 6100 mm plus sag corrections |  |
|  | (ii) Across and along all roads and paths | 6100 mm Plus sag corrections & allowances |  |
| 9. Insulators | (i) Type | Ball & Socket Type (16 mm for 90 kN disc &20 mm for 120 kN disc) / Long rod porcelain insulators |  |
|  | (ii) Size of disc | 255mm x 145 mm / as per IS 2486, IEC: 60120 |  |
|  | - Number of disc in each insulator - Suspension - Tension | 9 no. 10 no. |  |
|  | - Electro-mechanical strength - Suspension - Tension | 90 kN 120 kN |  |
| 10. Tension Limits | - For conductor and ground wire - at 320 C &no wind - at 320 C &full wind - at 00 C &36% of full wind | 25 % of UTS 70 % of UTS 70 % of UTS |  |

1.1.3	Basic Design Parameters for 220 KV TL

| Item | Particulars | 220 kV Line (Single/double- 3phase) with AAAC/ACSR |  |
| --- | --- | --- | --- |
| 1. SPAN | (i) Normal span (Design Span) | 350 M |  |
|  | (ii) Wind span | 350 M |  |
|  | (iii) Weight span, both span (total) - Maximum - Minimum | Suspension | Tension |
|  |  | 525 M 200 M | 525 M 0 M |
|  | (iii) Weight span, one span - Maximum - Minimum | Suspension | Tension |
|  |  | 315 M 100 M | 315 M -200 M |
| 2. TEMPARATURE RANGE | (I) Maximum | 850C |  |
|  | (ii) Minimum | 00C |  |
|  | (iii) Every Day | 320C |  |
| 3. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 4. CONDUCTOR | - Material | AAAC |  |
|  | - Number of strands & size | 37/4.00 mm |  |
|  | - No. of conductor per phase | 1 |  |
| 5. GROUND WIRE | - Type | OPGW |  |
|  | - Size | 7 / 3.15 mm |  |
|  | - No. of earth wire | 1 |  |
| 6. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 7. Wind pressure | Maximum wind pressure up to a height of 10 M about mean retarding force | 793 N/m2 |  |
| 8.GROUND CLEARANCE (Under maximum sag) | (i) Rough country | 7000 mm plus sag corrections |  |
|  | (ii) Across and along all roads and paths | 7000 mm Plus sag corrections & allowances |  |
| 9. INSULATORS | (i) Type | Ball & Socket Type (20 mm) / Porcelain long rod insulator |  |
|  | (ii) Size of disc | 255mm x 145 mm/ as per IS 2486 / IEC: 60120 |  |
|  | - Number of disc in each insulator - Suspension - Tension | 14 no. 15 no. |  |
|  | - Electro-mechanical strength - Suspension - Tension | 90 kN 120 kN |  |
| 10. Tension Limits | - For conductor and ground wire - at 320 C & no wind - at 320 C & full wind - at 00 C & 36% of full wind | 25 % of UTS 70 % of UTS 70 % of UTS |  |

1.1.4	Basic Design Parameters for 400 KV TL

| Item | Particulars | 400 kV Line (Single/double- 3phase) with ACSR/AAAC |  |
| --- | --- | --- | --- |
| 1. SPAN | (i) Normal span (Design Span) | 400 M |  |
|  | (ii) Wind span | 400 M |  |
|  | (iii) Weight span, both span (total) - Maximum - Minimum | Suspension | Tension |
|  |  | 600 M 200 M | 600 M 0 M |
|  | (iii) Weight span, one span - Maximum - Minimum | Suspension | Tension |
|  |  | 360 M 120 M | 360 M -360 M |
| 2. TEMPARATURE RANGE | (I) Maximum | 850C |  |
|  | (ii) Minimum | 00C |  |
|  | (iii) Every Day | 320C |  |
| 3. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 4. CONDUCTOR | - Material | ACSR Moose |  |
|  | - Number of strands & size | 54/3.53 mm Al 7/3.53 mm Steel |  |
|  | - No. of conductor per phase | 2 |  |
| 5. GROUND WIRE | - Type | Galvanised steel stranded wire, OPGW |  |
|  | - Size | 7 / 4 mm |  |
|  | - No. of earth wire | 2 |  |
| 6. Wind Speed Zone | Wind Speed Zone | Zone – 5 as per IS : 875 |  |
| 7. Wind pressure | Maximum wind pressure up to a height of 10 M about mean retarding force | 793 N/m2 |  |
| 8.GROUND CLEARANCE (Under maximum sag) | (i) Rough country | 8840 mm plus sag corrections |  |
|  | (ii) Across and along all roads and paths | 8840 mm Plus sag corrections & allowances |  |
| 9. INSULATORS | (i) Type | Ball & Socket Type (20 mm)/Porcelain long rod insulators |  |
|  | (ii) Size of disc | 255mm x 145 mm/ as per IS 2486 , IEC: 60120 |  |
|  | - Number of disc in each insulator - Suspension - Tension | 14 no. 15 no. |  |
|  | - Electro-mechanical strength - Suspension - Tension | 120kN 160 kN |  |
| 10. Tension Limits | - For conductor and ground wire - at 320 C & no wind - at 320 C & full wind - at 00 C & 36% of full wind | 25 % of UTS 70 % of UTS 70 % of UTS |  |