CHAPTER 44: TECHNICAL SPECIFICATION FOR INSULATOR STRING HARDWARE

44.1.0	 HARDWARE

Each insulator string assembly shall generally include the following hardware:

Anchor shackle for attachment of suspension string assembly to the tower hanger and tension string assembly to the tower strain plate. Suitable top and bottom yoke assemblies with the arrangement of fixing a set of arcing horns.

-	Set of arcing horns

-	Suspension or tension clamp

-	Bolts, nuts, washers, split pins etc.

-	Other fitting s necessary to make the strings complete such as ball clevis, socket clevis, chain links etc.

The tenderer shall be responsible and satisfy himself that all the hardware included in strings are entirely suitable for the conductor offered.

44.2.0	SUSPENSION CLAMP

The suspension clamps shall be made of malleable iron or aluminium alloy, hot dip galvanised and shall be suitable to accommodate the conductor together with one set of preformed armour rods. Suitable sheet aluminium liners shall be provided. The suspension clamps shall be designed to avoid any possibility of deforming or damaging the conductor. The lips shall be rounded off and the seating and the bell mouths shall be smooth to avoid corona and radio interference noises. The suspension clamps shall be suitable to carry the bottom part of the arcing horn and to receive the fittings of the insulator string.

The suspension clamps shall be such that the conductor should not slip at a load of 25% of the breaking load of the conductor. The ultimate strength of the clamp for vertical load shall not be less than the failing load of the Disc Insulators.

44.2.1	STRAIN CLAMP

The bolted strain clamps shall also be made of malleable iron or aluminium alloy; hot dip galvanised, lined with sheet aluminium liners and shall be suitable to accommodate the conductor with necessary binding tapes etc. The lips shall be rounded off carefully and conductor seating and the ball mouth shall be smooth to avoid corona and radio interference noises. Suitable attachment for receiving one side of arcing horns and for connecting to the insulator strings shall be provided.

The strain clamps shall be such that the conductor should not slip at a load of 90% of the breaking load of the conductor. The ultimate strength of the clamp for horizontal load shall not be less than the ultimate strength of the conductor

44.2.2	ARCING HORNS:

Arcing horns of approved size and dimensions shall be provided for every string of insulators. The performance data for arcing horns to be supplied shall be made available to the Employer.

44.2.3	OTHER INSULATOR STRING HARDWARE:

The strength of other string hardware namely anchor shackle, yoke plates, socket-clevis etc. shall be co-ordinated with insulator disc strength.

44.3.0	Interchangeability

The hardware together with ball and socket fittings shall be of standard design, so that this hardware is interchangeable with each other and suitable for use with disc insulators of any make con1orming to relevant Indian/International Standard.

44.4.0	Corona and RI Performance

Sharp edges and scratches on all the hardware fittings shall be avoided. All surfaces must be clean, smooth, without cuts and abrasions or projections. The Contractor/Manufacturer must give suitable assurance about the satisfactory corona and radio interference performance of the materials offered by him.

44.5.0	Maintenance

The hardware fittings offered shall be suitable for employment of hot line maintenance technique so that usual hot line operations can be carried out with ease, speed and safety. The technique adopted for hot line maintenance shall be generally bare hand method & hot stick method. The Bidder should clearly establish in the bid, the suitability of his fittings for hot line maintenance.

The line side yoke plate shall have a notch & a working hole of suitable size. The design of corona control rings/grading ring shall be such that it can be easily replaced by employing hot line maintenance technique.

44.6.0	Designation

Ball and Socket Designation

The dimensions of the ball and socket shall be 16 mm (Alt-B) designation for 70 KN &90KN Insulators, 20 mm designation for hardware with 120kN & 160 kN Insulators, in accordance with the standard dimensions stated in IS: 2486-(Part-II) /IEC:120. The dimensions shall be checked by the appropriate gauge after galvanising only.

44.7.0	Security Clips and Split Pins

44.7.1	Security clips for use with ball and socket coupling shall be R-shaped, hump type which provides positive locking 9f the coupling as per IS: 2486-(Part-III)/IEC: 372. The legs of the security clips shall be spread after assembly in the works to prevent complete withdrawal from the socket. The locking device should be resilient, corrosion resistant and of suitable mechanical strength. There shall be no risk of the locking device being displaced accidentally or being rotated when in position. Under no circumstances shall the locking devices allow separation of fittings.

44.7.2	The hole for the security clip shall be countersunk and the clip should be of such design that the eye of clip may be engaged by a hot line clip puller to provide for disengagement under energised conditions. The force required to pull the security clip into its unlocked position shall neither be less than 50 N (5 kg) nor more than 500 N (50 kg).

Split pins shall be used with bolts & nuts.

44.8.0	Arcing Horn for EHV Strings

44.8.1	The arcing horn shall be provided on tower side of the hardware fittings. The same shall be either ball ended rod type or tubular type.

44.8.2	The spark gap shall be so adjusted to ensure effective operation under actual field conditions.

44.9.0	Yoke Plates

•	The strength of yoke plates shall be adequate to withstand the minimum ultimate tensile strength as specified in the bid drawings.

•	The plates shall be either triangular or rectangular in shape as may be necessary. The design of yoke plate shall take into account the most unfavorable loading conditions likely to be experienced as a result of dimensional tolerances for disc insulators as well as components of hardware fittings within the specified range. The plates shall have suitable holes for fixing corona control rings/grading ring/arcing horn. All the corners and edges should be rounded off with a radius of atleast 3 mm. Design calculations i.e. for bearing & tensile strength, for deciding the dimensions of yoke plate shall be furnished by the Contractor/Manufacturer. The holes provided for bolts in the yoke plate should satisfy shear edge condition as per Clause No. 10.2.4.2 of IS:800-2007.

44.10.0 Corona Control Rings/Grading Ring (For 220 kV & above voltage level line)

•	The Corona control rings/grading ring shall be provided with hardware fittings and shall be of such design that it should cover at least one disc insulator in disc insulator strings/ metal polymer junction point in composite insulator strings so that they will reduce the voltage across the insulator units. It shall also improve corona and radio interference performance of the complete insulator string along with hardware fittings.

•	The corona control rings/grading ring shall be made of high strength heat treated aluminium alloy tube of minimum 2.5 mm wall thickness. If mild steel brackets are used then the brackets shall not be welded to the pipe but shall be fixed by means of bolts and nuts on a small aluminium plate attachment welded to the pipe. The welded center of the corona control ring/grading ring shall be grinded before buffing. Alternately, Aluminium tube/flats of suitable dimensions welded to the corona control rings/grading rings may be used for connection to yoke plate.

•	The Corona control rings/grading ring should have a brushed satin finish and not a bright glossy surface. No blemish should be seen or felt when rubbing a hand over the metal.

•	Bidder may quote for grading ring with armour grip suspension assembly. The grading ring shall be of open type design with a gap of 125 mm. The open ends shall be suitably terminated. The outside diameter of the tube shall be 75 mm. The ends of grading ring tube shall be sealed with welded aluminum cap duly buffed.

44.11.0 	Sag Adjustment Plate (For 400 kV voltage level line)

•	The sag-adjustment plate to be provided with the double tension hardware fitting (for 400kV (Twin) line) shall be of three plate type. The sag adjustment plate shall be provided with a safety locking arrangement. The device shall be of such design that the adjustment is done with ease, speed and safety.

•	The maximum length of the sag adjustment plate from the connecting part of the rest of the hardware fittings shall be 520 mm. The details of the minimum and maximum adjustment possible and the steps of adjustment shall be clearly indicated in the drawing. An adjustment of 150 mm minimum at the interval of 6 mm shall be possible with the sag adjustment plate.

•	Design calculations for deciding the dimensions of sag adjustment plate shall be furnished by Contractor/Manufacturer. The hole provided for bolts should satisfy shear edge condition as per Clause No. 10.2.4.2 of IS:800-2007.

44.12.0	 Turnbuckle

44.12.1 The turn buckle is to be provided with single tension hardware fitting. The threads shall be of sufficient strength to remain unaffected under the specified tensile load.

44.12.2 The maximum length of the turn buckle from the connecting part of the rest of the hardware fittings shall be 380 mm for 132KV and 220KV Line and 520mm for 400KV Line. The details of the minimum and maximum adjustment possible shall be clearly indicated in the drawing submitted with the bid. An adjustment of 135 mm minimum for 132KV and 220KV Line and 150mm minimum for 400KV Line shall be possible with turnbuckle.

44.13.0	 Suspension Assembly

44.13.1	The suspension assembly shall include free center type suspension clamp along with standard preformed armour rods or armour grip suspension clamp; except for Pilot insulator string for which only suitable Envelope type suspension clamp shall be used.

44.13.2	The suspension clamp along with standard preformed armour rods set shall be designed to have maximum mobility in any direction and minimum moment of inertia so as to have minimum stress on the conductor in the case of oscillation of the same.

44.13.3 The suspension assembly shall be designed, manufactured and finished to give it a suitable shape, so as to avoid any possibility of hammering between suspension assembly and conductor due to vibration. The suspension assembly shall be smooth and without any cuts, grooves, abrasions, projections, ridges or excrescence which might damage the conductor.

44.13.4 The suspension assembly/clamp shall be so designed so that it minimises the static and dynamic stress developed in the conductor under various loading conditions as well as during wind induced conductor vibrations. It shall also withstand power arcs and have required level of Corona/AIV performance.

44.14.0	 Free Center Type Suspension Clamp

For the Free Center Suspension Clamp seat shall be smoothly rounded and curved into a bell mouth at the ends. The lip edges shall have rounded bead. There shall be at least two U-bolts for tightening of clamp body and keeper pieces together.

44.15.0	 Standard Preformed Armour Rod Set

44.15.1 The Preformed Armour Rod Set suitable for Conductor shall be used to minimise the stress developed in the sub-conductor due to different static and dynamic loads because of vibration due to wind, slipping of conductor from the suspension clamp as a result of unbalanced conductor tension in adjacent spans and broken wire condition. It shall also withstand power arcs, chafing and abrasion from suspension clamp and localised heating effect due to magnetic power losses from suspension clamps as well as resistance losses of the conductor.

44.15.2 The preformed armour rods set shall have right hand lay and the inside diameter of the helices shall be less than the outside diameter of the conductor in order to gently but permanently grip the conductor. The surface of the armour rod when fitted on the conductor shall be smooth and free from projections, cuts and abrasions, etc.

44.15.3 The pitch length of the rods shall be determined by the Bidder but shall be less than that of the outer layer of conductor and the same shall be accurately controlled to maintain uniformity and consistently reproducible characteristic wholly independent of the skill of linemen.

44.15.4	The conductivity of each rod of the set shall not be less than 12% of the conductivity of the International Annealed Copper Standard (lACS).

44.16.0	Armour Grip Suspension Clamp

• The armour grip suspension clamp shall comprise of retaining strap, support housing,   elastomer inserts with aluminum reinforcements and AGS preformed rod set.

• Elastomer insert shall be resistant to the effects of temperature up to 95oC, Ozone, ultraviolet radiations and other atmospheric contaminants likely to be encountered in service. The physical properties of the elastomer shall be of approved standard. It shall be electrically shielded by a cage of AGS performed rod set. The elastomer insert shall be so designed that the curvature of the AGS rod shall follow the contour of the neoprene insert.

• The length of the AGS preformed rods shall be such that it shall ensure sufficient slipping strength as specified in the Standard Technical Particulars and shall not introduce unfavourable stress on the conductor under all operating conditions.

44.17.0	Envelope Type Suspension Clamp

• The seat of the envelope type suspension clamp shall be smoothly rounded & suitably curved at the ends. The lip edges shall have rounded bead. There shall be at least two U-bolts for tightening of clamp body and keeper pieces together. Hexagonal bolts and nuts with split-pins shall be used for attachment of the clamp.

44.18.0	Dead End Assembly

44.18.1 The dead-end assembly shall be suitable for Conductor as detailed in the document.

44.18.2 The dead-end assembly shall be compression type with provision for comprising the jumper terminal at one end. The angle of the jumper terminal to be mounted should be 30⁰ with respect to the vertical line. The area of bearing surface on all the connections shall be sufficient to ensure positive electrical and mechanical contact and avoid local heating due to I2R losses. The resistance of the clamp when compressed on Conductor shall not be more than 75% of the resistance of equivalent length of Conductor.

44.18.3 The assembly shall not permit slipping of, damage to, or failure of the complete conductor or any part thereof at a load less than 95% of the ultimate tensile strength of the conductor.

44.19.0	Fasteners: Bolts, Nuts and 'Washers

44.19.1 All bolts and nuts shall conform to IS: 6637. All bolts and nuts shall be galvanised as per IS-1367 -(Part 13)/IS-2629. All bolts and nuts shall have hexagonal heads, the heads being forged out of solid truly concentric, and square with the shank, which must be perfectly straight.

44.19.2 Bolts up to M16 and having length up to 10 times the diameter of the bolt should be manufactured by cold forging and thread rolling process to obtain good and reliable mechanical properties arid effective dimensional control. The shear strength of bolt for 5.6 grade should be 310 MPa minimum as per IS-12427. Bolts should be provided with washer face in accordance with IS: 1363 Part-1 to ensure proper bearing.

44.19.3 Nuts should be double chamfered as per the requirement of IS: 1363 Part-III. It should be ensured by the manufacturer that nuts should not be over tapped beyond 0.4 mm oversize on effective diameter for size up to M16

44.19.4 Fully threaded bolts shall not be used. The length of the bolt shall be such that the threaded portion shall not extend into the place of contact of the component parts.

44.19.5 All bolts shall be threaded to take the full depth of the nuts and threaded enough to permit the firm gripping of the component parts but no further .it shall be ensured that the threaded portion of the bolt protrudes not less than 3 mm and not more than 8 mm when fully tightened. All nuts shall fit and tight to the point where shank of the bolt connects to the head.

44.19.6 For parts/ components requiring grip strength viz. arcing horn, corona rings & dead-end jumper assembly, fully threaded bolts can be used as an alternative. Bolts & nuts for these parts/ components shall be of minimum 4.6 grade conforming to IS 6639 or equivalent International standards.

44.19.7 Flat washers and spring washers shall be provided wherever necessary and shall be of positive lock type. Spring washers shall be electro-galvanised. The thickness of washers shall conform to IS: 2016.

44.19.8 The Bidder shall furnish bolt schedules giving thickness of components connected, the nut and the washer and the length of shank and the threaded portion of bolts and size of holes and any other special details of this nature.

44.19.9 To obviate bending stress in bolt, it shall not connect aggregate thickness more than three time its diameter.

44.19.10 Bolts at the joints shall be so staggered that nuts may be tightened with spanners without fouling.

44.19.11 Fasteners of grade higher than 8.8 are not to be used.

44.20.0	Materials

The materials of the various components shall be as specified hereunder. The Bidders hall indicate the material proposed to be used for each and every component of hardware fitting stating clearly the class, grade or alloy designation of the material, manufacturing process & heat treatment details and the reference standards.

| Sl. No. | Name of item | Material treatment | Process of Standard | Reference | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1 | Security Clips | Stainless Steel/ Phospher Bronze | - | AISI 302 or 304-L/ IS-1385 |  |
| 2 | Arcing Horn | Mild Steel Rod/ Tube Type | Hot dip galvanised | As per IS-226 or IS-2062 |  |
| 3 | Ball Fittings, Socket, all shackles links cleves | Class-IV Steel | Drop forged & normalized Hot dip galvanised | As per IS: 2004 |  |
| 4 | Yoke Plate | Mild Steel | Hot dip galvanized | As per IS-226 or IS-2062 |  |
| 5 | Sag Adjustment plate | Mild Steel | Hot dip galvanized | As per IS-226 or IS-2062 |  |
| 6(a). | Corona Control ring/ Grading ring | High Strength Al. Alloy tube (6061/ 6063/1100 type or 65032/ 63400 Type) | Heat treated Hot dip galvanized | ASTM-B429 or as per IS | Mechanical strength of welded joint shall not be less than 20 KN |
| 6(b). | Supporting Brackets & Mounting Bolts | High Strength Al Alloy 7061/ 6063/ 65032/63400 Type) or Mild Steel | Heat treated Hot dip galvanized | ASTM-B429 or as per IS:226 or IS:2062 |  |
| 7(a). | Envelope type Clamp: Clamp Body, Keeper Piece | High Strength Al. Alloy 4600/ LM-6 or 6061/65032 or 6063/63400 | Casted or forged & Heat treated | IS:617 or ASTM-B429 |  |
| 7(b). | Envelope type Clamp: Cotter bolts/ Hangers, Shackles, Brackets | Mild Steel | Hot dip galvanised | As per IS-226 or IS-2062 |  |
| 7(c) | Envelope type Clamp: U Bolts | Stainless Steel or High Strength Al alloy 6061/ 6063 or 65032/63400 | Forged & Heat treated | AISI 302 or 304-L ASTM-B429 |  |
| 8(a). | Dead End Assembly: Outer Sleeve. | EC grade Al of purity not less than 99.50% |  |  |  |
| 8(b). | Steel Sleeve. | Mild Steel | Hot Dip Galvanised | IS:226/ IS-2062 |  |
| 9. | AGS clamp (a) Supporting house. | High strength corrosion resistant Al. alloy LM6, 4600 or equivalent 6061 | Cast/forged heat treated. | IS:617 or equivalent |  |
|  | (b) Al insert and retaining strap. | High strength Al alloy type 6061 or equivalent | Forged and Heat treated | ASTM:B429. |  |
|  | (c) Elastomer cushion. | Moulded on Al reinforcement |  |  |  |
| 10. | P. A. rod. | High strength Al alloy type 6061 or equivalent | Heat treatment during manufacturing | ASTM:B429 | Min. tensile strength of 35 kg/mm2 |
| 11. | Turn Buckle. | Class-II Steel | Forged hot dip galvanized | IS:2004 |  |

44.21.0	 Workmanship

44.21.1 All the equipment shall be of the latest design and conform to the best modern practices adopted in the Extra High Voltage field. The Bidder shall offer only such equipment as guaranteed by him to be satisfactory and suitable for rated voltage of transmission lines and will give continued good performance.

44.21.2 The design, manufacturing process and quality control of all the materials shall be such as to give the specified mechanical rating, highest mobility, elimination of sharp edges and comers to limit corona and radio-interference, best resistance to corrosion and a good finish.

44.21.3 All ferrous parts including fasteners shall be hot dip galvanized, after all machining has been completed. Nuts may, however, be tapped (threaded) after galvanizing and the threads oiled. Spring washers shall be electro galvanized. The bolt threads shall be undercut to take care of the increase in diameter due to galvanizing. Galvanizing shall he done in accordance with IS: 2629 / IS-1367 (Part 13) or equivalent International Standards and shall satisfy the tests mentioned in IS: 2633-1986or equivalent International Standards. Fasteners shall withstand four dips while spring washers shall withstand three dips of one-minute duration in the standard Preece test. Other galvanized materials shall have a minimum average coating of zinc equivalent to 610 gm / sq.m shall be guaranteed to withstand at least six successive dips each lasting one (1) minute under the standard price test for galvanizing.

44.21.4 Before ball fittings are galvanized, all die flashing on the shank and on the bearing surface of the ball shall be carefully removed without reducing the dimensions below the design requirements.

44.21.5 The zinc coating shall be perfectly adherent of uniform thickness, smooth, reasonably bright. Continuous and free from imperfections such as flux, ash, rust, stains, bulky white deposits and blisters. The zinc used for galvanizing shall be grade Zn 99.95 as per IS: 209or equivalent International Standards.

44.21.6 Pin balls shall be checked with the applicable “GO” gauges in at least two directions. one of which shall be across the line of die flashing, and the other 90o to this line. "NO GO" gauges shall not pass in any direction.

44.21.7 Socket ends, before galvanizing, shall be of uniform contour. The bearing surface of socket ends shall be uniform about the entire circumference without depressions, of high spots. The internal contours of socket ends shall be concentric with the axis of the fittings as per IS: 2486or equivalent International Standards.

The axis of the bearing surfaces of socket ends shall be coaxial with the axis of the fittings. There shall be no noticeable tilting of the bearing surfaces with the axis of the fittings.

44.21.8 In case of casting, the same shall be free from all internal defects like shrinkage, inclusion, blow holes, etc. Pressure die casting shall not be used for casting of components with thickness more than 5 mm

44.21.9 All current carrying parts shall be so designed and manufactured that contact resistance is reduced to minimum.

44.21.10 No equipment shall have sharp ends or edges, abrasions or projections and cause any damage to the inductor in any way during erection or during continuous operation which would product high electrical and mechanical stresses in normal working. The design of adjacent metal parts and mating surfaces shall be such as to prevent corrosion of the contact surface and to maintain good electrical contact under service conditions.

44.21.11 All the holes shall be cylindrical, clean cut and perpendicular to the plane of the material. The periphery of the holes shall be free from burrs.

44.21.12 All fasteners shall have suitable corona free locking arrangement to guard against Vibration loosening.

44.21.13 Welding of aluminium shall be by inert gas shielded tungsten arc or inert gas shielded metal arc process. Welds shall be clean, sound, smooth, uniform without overlaps, properly fused and completely sealed. There shall be no cracks, voids incomplete penetration, incomplete fusion, under-cutting or inclusions. Porosity shall be minimised so that mechanical properties of the aluminium alloys are not affected. All welds shall be properly finished as per good engineering practices.

44.22.0	 Bid Drawings

44.22.1 The Bidder shall furnish full description and illustrations of materials offered.

44.22.2 Fully dimensioned drawings of the complete insulator string hardware and their component parts showing clearly the following arrangements shall be furnished in five (5) copies along with the bid. Weight, material and fabrication details of all the components should be included in the drawings.

(i)	Attachment of the hanger or strain plate.

(ii)	Yoke Plate

(iii)	Suspension or dead-end assembly.

(iv)	Arcing horn attachment to the string

(v)	Hardware fittings of ball and socket type for inter connecting units.

(iv)	Corona control rings/grading ring attachment to conductor and other small accessories.

44.22.3 All drawings shall be identified by a drawing number and contract number. All drawings shall be neatly arranged. All drafting & lettering shall be legible. The minimum size of lettering shall be 3 mm. All dimensions & dimensional tolerances shall be mentioned in mm.

The drawings shall include:

(i) Dimensions and dimensional tolerance.

(ii) Material, fabrication details including any weld details & any specified finishes & coatings. Regarding material designation & reference of standards are to be indicated.

(iii) Catalogue No.

(iv) Marking

(v) Weight of assembly

(vi) Installation instructions

(vii) Design installation torque for the bolt or cap screw.

(viii) Withstand torque that may be applied to the bolt or cap screw without failure of component parts.

(ix) The compression die number with recommended compression pressure.

(x) All other relevant terminal details.

44.22.4 After placement of award, the Contractor shall submit fully dimensioned drawings including all the components in four (4) copies to the Employer for approval. After getting approval from the Employer and successful completion of all the type tests, the Contractor shall submit thirty (10) more copies of the same drawings to the Employer for further distribution and field use at Employer’s end.

44.23.0 	Completeness of works

Bidder shall assess the complete requirement of line hardware, hardware accessories and assemblies in complete for the erection of the lines as per the recommended erection practices.

The hardware assemblies shall be supplied complete with components, sub-components, nuts, bolts, washer etc. fittings and accessories for conductor & earth wire like Mid Span Joints, Repair Sleeves, and Stockbridge Vibration Dampers.

The Contractor shall also supply all line and tower accessories.

44.24.0	 Standards

44.24.1 The Hardware Fittings, conductor and earth wire accessories shall conform to the following Indian Standards or equivalent International Standards, which shall mean latest revisions, amendments/changes adopted and published unless specifically stated otherwise in the specification.

1.	IS: 209		Specification for Zinc.

2.	IS: 398		Specification for Aluminum Conductors.

for Overhead Transmission Purposes,

3.	IS: 1327	Method of Determination of Weight of

Zinc Coating on Tin Plate.

4.	IS: 1573	Electroplated Coating of Zinc on Iron and Steel

5.	IS: 2121	Specification for Conductors and Earthwire

Accessories for Overhead Power Lines

(Part-1 )	Armour Rods, Binding Wires and Tapes for

Conductors

(Part-2)		Mid-span joints and Repair Sleeves for

Conductors

6.	IS : 2486	Specification for Insulator Fittings for Overhead Power Lines

With a Nominal Voltage Greater than 1 000 V

(Part 1)	General Requirements and Tests

7.	IS:2629		Recommended Practice for Hot Dip

Galvanizing of Iron and Steel

8.	IS:2633		Method of Testing Uniformity of Coating

on Zinc Coated Articles

9.	IS:4826		Galvanized Coating on Round Steel Wires

10.	IS : 6639	Hexagonal Bolts for Steel Structures

11.	IS: 6745	Methods for Determination of Weight of Zinc Coating on

Zinc Coated Iron and Steel Articles

12.	IS : 8263	Method for Radio Interference Tests on High Voltage Insulators

13.	IS : 9708	Specification for Stock Bridge vibration Dampers for Overhead Power Lines

44.25.0	 TESTS

The insulator discs and hardware fittings shall be subjected to the tests before despatch, in accordance with the relevant standards. The successful contractor shall submit the test results in quadruplicate to the Employer.

44.26.0 	MARKING

Each insulator disc shall be legibly and indelibly marked with the following:

-	Name or trade mark of the manufacturer.

-	Month and year of manufacture.

-	Minimum failing load in Newton.

-	Country of manufacture

-	Standard certification mark, if any.

The marking of the porcelain shall be printed and shall be applied before firing.

44.27.0 STANDARDIZED TECHNICAL PARAMETERS

A)	Standardized Technical Particulars of Hardware Fittings for 400 kV Transmission Line with Quad ACSR MOOSE Conductor

| 1. | Suspension hardware fittings for Quad ACSR MOOSE conductor |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars / Value |  |  |
|  |  |  | Double ‘I’ / Double ‘I’ (RC)# |  | Single ‘I’ Pilot |
|  |  |  | AGS clamp | Free centre clamp | Envelope clamp |
| 1. | Maximum magnetic power loss of suspension assembly at sub conductor current of 600 amperes, 50Hz AC | Watt | 4 |  | 8 |
| 2. | Slipping strength of suspension assembly(clamp torque Vs slip curve shall be enclosed) | kN | 20-29 |  |  |
| 3. | Particulars of standard/AGS Standard / AGS preformed armour rod set for suspension assembly |  |  |  |  |
|  | a) No. of rods per set | No. | 12 |  | NA |
|  | b) Direction of lay |  | Right Hand |  | NA |
|  | c) Overall length after fitting on conductor | mm | 2235 | 2540 | NA |
|  | d) Diameter of each rod | mm | 9.27 |  | NA |
|  | e) Tolerance in |  |  |  | NA |
|  | i) Diameter of each rod | ±mm | 0.10 |  | NA |
|  | ii) Length of each rod | ±mm | 25 |  | NA |
|  | iii) Difference of length between the longest and shortest rod in a set | ±mm | 13 |  | NA |
|  | g) Type of Aluminium alloy used for manufacture of PA rod set |  | 6061/ 65032 |  | NA |
|  | h) UTS of each rod | Kg/mm2 (Min) | 35 |  | NA |
| 4. | Particulars of Elastomer (For AGS Clamp only) |  |  |  |  |
|  | a) Type of elastomer |  | Chloroprene / Neoprene | NA | NA |
|  | b) Shore hardness of elastomer |  | 65 - 80 | NA | NA |
|  | c) Temperature range for which elastomer is designed | °C | Upto 95°C | NA | NA |
|  | d) Moulded on insert |  | Yes | NA | NA |
| 5. | Mechanical Strength of Suspension fitting (excluding suspension clamp) | KN | Double I :240 Double ‘I’ (RC): 640 |  | 120 |
| 6. | Mechanical Strength of suspension clamp. |  | 70 | 70 | 70 |
| 7. | Purity of Zinc used for galvanising | % | As per IS:209 / IS 13229 |  |  |
| 8. | Min. No. of dips in standard preece test the ferrous parts can withstand | No | - Fasteners : 4 dips of 1 min - Spring washers : 3 dips of 1 min - All others : 6 dips of 1 min |  |  |

| 2. | Tension hardware fittings for Quad ACSR MOOSE conductor |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars / Value |  |  |  |
|  |  |  | Single Tension | Quad Tension | Quad Tension# (RC) |  |
| 1. | Mechanical Strength of Tension fittings (excluding dead end clamp) | kN | 120 | 640 | 920 |  |
| 2. | Type of Dead End assembly |  | Compression |  |  |  |
| 3. | Compression Pressure | MT | 100 |  |  |  |
| 4. | Maximum electrical resistance of dead end assembly as a percentage of equivalent length of Conductor | % | 75 |  |  |  |
| 5. | Slip strength of dead end assembly | kN | 153.2 |  |  | 214 |
| 6. | Purity of Zinc used for galvanising | % | As per IS:209 / IS 13229 |  |  |  |
| 7. | Min. No. of dips in standard preece test the ferrous parts can withstand. | Nos | - Fasteners : 4 dips of 1 min - Spring washers : 3 dips of 1 min - All others : 6 dips of 1 min |  |  |  |

#: To be used with AACSR MOOSE Conductor

B)	Standardized Technical Particulars of Hardware Fittings for 400 kV Transmission Line with twin ACSR MOOSE Conductor

| 1. | Suspension hardware fittings for twin ACSR MOOSE* conductor |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |  |  |  |  |
|  |  |  | Single “I” Suspension Fittings with |  |  | Double “V” Suspension Fittings with (AACSR MOOSE Conductor) |  |  | Single suspension Pilot Fitting with |
|  |  |  | AGS clamp | Free Centre clamp |  | AGS clamp | Free Centre clamp |  | Envelope clamp |
| 1. | Maximum magnetic power loss of one suspension assembly at sub-conductor current of 600 amperes | Watt | 4 |  |  | 4 |  |  | 8 |
| 2. | Slipping strength of suspension assembly | KN | 20-29 |  |  | 20-29 |  |  | 20-29 |
| 3. | Particulars of standard/ AGS preformed armour rod set for suspension assembly |  |  |  |  |  |  |  |  |
|  | a) No. of rods per set | No. | 12 |  |  | 12 |  |  | NA |
|  | b) Direction of lay |  | Right hand |  |  | Right hand |  |  | NA |
|  | c) Overall length after fitting on conductor | mm | 2235 | 2540 |  | 2235 | 2540 |  | NA |
|  | d) Diameter of each rod | mm | 9.27 |  |  | 9.27 |  |  | NA |
|  | e) Tolerance in |  |  |  |  |  |  |  |  |
|  | i) Diameter of each rod | ±mm | 0.10 |  |  | 0.10 |  |  | NA |
|  | ii) Length of each rod | ±mm | 25 |  |  | 25 |  |  | NA |
|  | iii) Difference of length between the longest and shortest rod in a set | ±mm | 13 |  |  | 13 |  |  | NA |
|  | f) Type of Aluminium alloy used for manufacture of PA rod set |  | 6061/ 65032 |  |  | 6061/ 65032 |  |  | NA |
|  | g) Minimum UTS of each rod | Kg/mm2 | 35 |  |  | 35 |  |  | NA |
| 4. | Particulars of Elastomer (For AGS Clamp only) |  |  |  |  |  |  |  |  |
|  | a) Type of elastomer |  | Chloroprene/Neoprene Rubber |  | NA | Chloroprene /Neoprene Rubber |  | NA | NA |
|  | b) Shore hardness of elastomer |  | 65 to 80 |  | NA | 65 to 80 |  | NA | NA |
|  | c) Temperature range for which elastomer is designed |  | Upto 95o C |  | NA | Upto 95o C |  | NA | NA |
|  | d) Moulded on insert |  | Yes |  | NA | Yes |  | NA | NA |
| 5. | Mechanical strength of suspension fitting(excluding suspension clamp) | KN | 120 |  |  | 2 x160 (along one limb) |  |  | 120 |
| 6. | Mechanical strength of suspension clamp | KN | 70 |  |  | 120 |  |  | 70 |
| 7. | Galvanising |  |  |  |  |  |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |  |  |  |  |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |  |  |  |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute c) all others: 6 dips of 1 minute |  |  |  |  |  |  |

* : except Double ‘V’ Suspension and Triple Tension fittings

| 1. | Tension hardware fittings for twin ACSR MOOSE* conductor |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |
|  |  |  | Single Tension | Double Tension | Triple Tension (AACSR MOOSE Conductor) |
| 1. | Mechanical strength of Tension fitting(excluding dead end clamp) | KN | 120 | 2x160 | 3x160 |
| 2. | Type of dead end assembly |  | Compression |  |  |
| 3. | Compression pressure | MT | 100 |  |  |
| 4. | Maximum electrical resistance of dead end assembly as a percentage of equivalent length of Conductor | % | 75 |  |  |
| 5. | Slip strength of dead end assembly | KN | 153.2 |  | 214 (AACSR ‘MOOSE’ to be used) |
| 6. | Galvanising |  |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5(IS 13229) |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand. | Nos. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute c) all others: 6 dips of 1 minute |  |  |

* : except Double ‘V’ Suspension and Triple Tension fittings

C)	Accessories for ACSR MOOSE conductor for 400 kV transmission line

| Mid span compression Joint for ACSR MOOSE Conductor |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |
|  |  |  | Aluminium Sleeve | Steel Sleeve |
| 1. | Material of Joint |  | Aluminium of purity 99.5% | Mild Steel(Fe-410, IS:2062) |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) | BHN | From 100 to 200 |  |
| 3. | Weight of Zinc coating for steel sleeve | gm/m2 | 610 |  |
| 4. | Dimension of sleeve Before compression |  | Aluminum sleeve | Steel sleeve |
| i) | Inside diameter | mm | 34.00 ± 0.5 | 11.50 ± 0.2 |
| ii) | Outside diameter | mm | 54.00 ± 1.0 | 21.00 ± 0.5 |
| iii) | Length | mm | 735 ± 5 | 250 ± 5 |
| 5. | Dimensions of Sleeve after compression |  | Aluminum sleeve | Steel sleeve |
| i) | Outside dimension(Corner to corner) | mm | 53.00 ± 0.5 | 20.20 ± 0.5 |
| ii) | Outside dimension ( face to face) | mm | 46.00 ± 0.5 | 17.50 ± 0.5 |
| iii) | Length | mm | 785 (approx) | 286 (approx) |
| 5. | Slip strength | KN | 153.2 |  |
| 6. | Maximum resistance of the compressed unit expressed, as percentage of the resistance of equivalent length of bare conductor. | % | 75 |  |
| 7. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |  |
| 8. | Maximum Radio Interference Voltage at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro Volts | 1000 |  |

| Repair sleeve for ACSR MOOSE Conductor |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Material |  | Aluminium of min purity 99.5% |
| 2. | Dimension of Aluminum sleeve Before compression |  |  |
| i) | Inside diameter | mm | 34.00 ± 0.5 |
| ii) | Outside diameter | mm | 54.00 ± 1.0 |
| iii) | Length | mm | 300.00 ± 5.0 |
| 3. | Dimensions of Aluminum Sleeve after compression |  |  |
| i) | Outside dimension(Corner to corner) | mm | 53.00 ± 0.5 |
| ii) | Outside dimension (face to face) | mm | 46.00 ± 0.5 |
| iii) | Length | mm | 330.00(Approx.) |
| 4. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |
| 5. | Maximum Radio Interference Voltage at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro Volts | 1000 |

| T-connector for ACSR MOOSE Conductor |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Material |  | Aluminium of purity 99.5% |
| 2. | Dimension of Aluminum sleeve Before compression |  |  |
|  | i) Inside diameter | mm | 34.00 ± 0.5 |
|  | ii) Outside diameter | mm | 54.00 ± 1.0 |
|  | iii) Length | mm | 400.00 ± 5.0 |
| 3. | Dimensions of Aluminum Sleeve after compression |  |  |
|  | i) Outside dimension(Corner to corner) | mm | 53.00 ± 0.5 |
|  | ii) Outside dimension ( face to face) | mm | 46.00 ± 0.5 |
| 4. | Axial tensile strength of welded portion of T-connector | KN | 30 |
| 5. | Maximum resistance of the compressed unit expressed, as percentage of the resistance of equivalent length of bare conductor. | % | 75 |
| 6. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |
| 7. | Maximum Radio Interference Voltage at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro Volts | 1000 |

| Vibration Damper for ACSR MOOSE conductor (For twin bundle conductor line only) |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Type of Damper |  | 4R-Stockbridge type |
| 2. | Materials of components |  |  |
|  | a) Damper masses |  | Cast iron/mild steel/Zinc alloy duly hot dip galvanised |
|  | b) Clamp |  | Aluminum alloy 4600 |
|  | c) Messenger cable |  | High tensile strength galvanized steel |
| 3. | Number of strands in stranded messenger cable | Nos. | 19 |
| 4. | Minimum ultimate tensile strength of stranded messenger cable | Kg/mm2 | 135 |
| 5. | Slip strength of stranded messenger cable (mass pull off) | KN | 5 |
| 6. | Slipping strength of damper clamp |  |  |
|  | (a) Before fatigue test | KN | 2.5 |
|  | (b) After fatigue test | KN | 2 |
| 7. | Resonance frequencies range | Hz | 5 to 40 |
| 8. | Maximum magnetic power loss per vibration damper watts for 600 amps, 50 Hz Alternating Current | Watts | 1 |
| 9. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |
| 10. | Maximum Radio Interference Voltage (RIV) at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro Volts | 1000 |
| 11. | Percentage variation in reactance after fatigue test in comparison with that . before fatigue test | % | +/-40 (Maximum) |
| 12. | Percentage variation in power dissipation after fatigue test in comparison with that before fatigue test | % | +/-40 (Maximum) |
| 13. | Galvanising |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5(IS 13229) |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand. | Nos. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute c) all others: 6 dips of 1 minute |

| Bundle Spacer for ACSR MOOSE conductor (For twin bundle conductor line only) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |
| 1. | Type of Bundle Spacer |  | Armour grip type |  |  |
| 2. |  |  | Insert | Main body | Retaining rods (if any) |
| (i) | Materials of components |  | Aluminum alloy 6061/65032 | Tube Aluminum alloy 6063/63400; 6061/ 65032 | Aluminum alloy 6061/65032 |
| (ii) | Manufacturing process of component parts |  | Forged | Tube- extrusion | Heat treatment during manufacturing |
| 3. | Retaining rods (if used) |  |  |  |  |
|  | (a) Number of retaining rods used for each spacer | no. | 8 |  |  |
|  | (b) Diameter | mm | 7.87 ± 0.1 |  |  |
|  | (c) Length | mm | 1100+15 |  |  |
|  | (d) Minimum UTS of rods | Kg/mm2 | 35 |  |  |
| 4. | Elastomer |  |  |  |  |
|  | (a) Type |  | Chloroprene/Neoprene |  |  |
|  | (c) Moulded on insert |  | Yes |  |  |
|  | (d) Shore hardness |  | 65 to 80 |  |  |
|  | (e) Thickness on insert | mm | 5(Average) |  |  |
|  | (f) Temp. range for which designed | °C | 95 |  |  |
| 5. | Minimum ultimate tensile strength of spacer |  |  |  |  |
|  | (a) Compressive load | kN | 14 |  |  |
|  | (b) Tensile load | kN | 7 |  |  |
| 6. | Slipping strength of spacer clamp |  |  |  |  |
|  | a) Before vibration test | KN | 2.5 |  |  |
|  | b) After vibration test | KN | 2 |  |  |
| 7. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |  |  |
| 8. | Maximum Radio Interference Voltage (RIV) at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro volts | 1000 |  |  |

| Rigid Spacer for Jumper for ACSR MOOSE conductor (For twin bundle conductor line only) |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Type of Spacer |  | Rigid type without retaining rods |
| 2. | Material of component parts |  |  |
|  | (a) Clamp |  | Aluminum alloy (4600) |
|  | (b) Main body |  | Aluminum alloy 6063/63400 ; 6061/65032 |
| 3. | Manufacturing process of component parts |  |  |
|  | (a) Clamp |  | Die-casting |
|  | (b) Main body |  | Aluminum extrusion |
| 4. | Minimum ultimate tensile strength of spacer |  |  |
|  | (a) Compressive load | kN | 14 |
|  | (b) Tensile load | kN | 7.0 |
| 5. | Slipping strength of spacer clamp | kN | 2.5 |
| 6. | Maximum Magnetic power loss per spacer for 600 Amps, 50 Hz Alternating Current | Watts | 1 |
| 7. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |
| 8. | Maximum Radio Interference Voltage (RIV) at 1 MHz for phase to earth voltage of 305 kV (rms) under dry condition | Micro volts | 1000 |

| Quad Rigid Spacer for Jumper for ACSR MOOSE conductor (For quadruple bundle conductor line only) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars / Value |  |  |
| 1. | Material of |  |  |  |  |
|  | (a) Clamp |  | Al Alloy IS:4600 or Equivalent |  |  |
|  | ( b) Body |  | Galvanised Steel / Al Alloy 4600 or Equivalent |  |  |
| 2. | Elastomer (if used) |  |  |  |  |
|  | (a) Shore hardness |  | 65 - 80 |  |  |
|  | (b) Temp. range for which designed | °C | Upto 95°C |  |  |
| 3. | Minimum ultimate tensile strength of spacer |  |  |  |  |
|  | (a) Compressive load | kN | 14 |  |  |
|  | (b) Tensile load | kN | 7.0 |  |  |
| 4. | Slipping strength of spacer clamp | kN | Clamp type | Longitudnal Load (kN) | Maxm Slip permitted (mm) |
|  |  |  | Metal – Metal Bolted | 6.5 | 1 |
|  |  |  | Rubber loaded | 2.5 | 2.5 |
|  |  |  | Preformed rod | 2.5 | 12 |
| 5. | Maximum magnetic power loss of at sub conductor current of 600 amperes, 50Hz AC | Watts | Below 1 watt. |  |  |
| 6. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |  |  |
| 7. | Radio Interference Voltage at 1 MHz for phase to earth voltage of 305 kV (rms) Microvolts under dry condition | μV | Below 1000 |  |  |

| Spacer damper for Quad ACSR MOOSE conductor |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars / Value |  |  |
| 1. | Type of Clamps |  | Preformed rods. |  |  |
| 2. | Type of Damping element |  | Spring / Elastomer / EPDM |  |  |
| 3. | Material of |  |  |  |  |
|  | (a) Clamp |  | Al Alloy IS:4600 or Equivalent for Casting & Al Alloy 6061 or Equivalent (for Forging) |  |  |
|  | ( b) Body |  |  |  |  |
| 4. | Elastomer (if used) |  |  |  |  |
|  | (a) Shore hardness |  | 50 - 80 |  |  |
|  | (b) Temp. range for which designed | °C | Upto 95°C |  |  |
| 5. | Minimum ultimate tensile strength of spacer |  |  |  |  |
|  | (a) Compressive load | kN | 14 |  |  |
|  | (b) Tensile load | kN | 7.0 |  |  |
| 6. | Slipping strength of spacer clamp |  |  |  |  |
|  | (a) Before vibration test | kN | Clamp type | Longitudnal Load (kN) | Maxm Slip permitted (mm) |
|  |  |  | Preformed rods | 2.5 | 12 |
|  | (b) After vibration test | kN | 80% of the above values |  |  |
| 7. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 320 |  |  |
| 8. | Radio Interference Voltage at 1 MHz for phase to earth voltage of 305 kV (rms) Microvolts under dry condition | μV | Below 1000 |  |  |

C)	Accessories for 7/3.66 mm GS Earthwire for 400 Kv/765 Kv  transmission line

| Mid span compression Joint for 7/3.66 mm GS Earthwire |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit |  | Particulars/ Value |  |  |  |
|  |  |  |  | Aluminium / Filler Sleeve |  | Steel Sleeve |  |
| 1. | Material of Joint |  |  | Aluminium of minimum purity 99.5% |  | Mild Steel(Fe-410, IS:2062) |  |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) | BHN |  | From 100 to 200 |  |  |  |
| 3. | Weight of Zinc coating | gm/m2 |  | 600 |  |  |  |
| 4. | Dimension of sleeve Before compression |  |  |  |  |  |  |
|  |  |  | Aluminium Sleeve |  | Steel Sleeve |  | Alu filler sleeve |
| i) | Inside diameter | mm | 22.00 ± 0.5 |  | 11.50 ± 0.2 |  | 11.50 ± 0.2 |
| ii) | Outside diameter | mm | 32.00 ± 0.5 |  | 21.00 ± 0.5 |  | 21.00 ± 0.5 |
| iii) | Length | mm | 400 ± 5 |  | 230 ± 5 |  | 60 ± 5 |
| 5. | Dimensions of Sleeve after compression |  |  |  |  |  |  |
|  |  |  |  | Aluminium Sleeve |  | Steel Sleeve |  |
| i) | Outside dimension(Corner to Corner) | mm |  | 29.40 ± 0.5 |  | 20.20 ± 0.5 |  |
| ii) | Outside dimension (face to face) | mm |  | 25.00 ± 0.5 |  | 17.50 ± 0.5 |  |
| iii) | Length | mm |  | 430 (approx) |  | 265 (approx) |  |
| 6. | Slip strength | KN |  | 65 |  |  |  |
| 7. | Maximum resistance of the compressed unit expressed, as percentage of the resistance of equivalent length of bare Earthwire | % |  | 75 |  |  |  |

| Flexible Aluminium Bond for 7/3.66 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Stranding |  | 19 (12+6+1) / dia 2.54 |
| 2. | Cross sectional area | Sq.mm | 95 |
| 4. | Length of aluminium cable | mm | 750 + 5 |
| 5. | Material of lugs |  | Aluminium alloy |
| 6. | Bolt Size |  |  |
|  | i) Diameter | mm | 16 |
|  | ii) Length | mm | 40 |

| Vibration Damper for 7/3.66 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Type of Damper |  | 4R-Stockbridge type |
| 2. | Materials of components |  |  |
|  | a) Damper masses |  | Cast iron/mild steel/Zinc alloy duly hop dip galvanised |
|  | b) Clamp |  | Aluminum alloy 4600 |
|  | c) Messenger cable |  | High tensile strength galvanized steel |
| 3. | Number of strands in stranded messenger cable | Nos. | 19 |
| 4. | Minimum ultimate tensile strength of stranded messenger cable | Kg/mm2 | 135 |
| 5. | Slip strength of stranded messenger cable (mass pull off) | kN | 2.5 |
| 6. | Slipping strength of damper clamp |  |  |
|  | (a) Before fatigue test | kN | 2.5 |
|  | (b) After fatigue test | kN | 2 |
| 7. | Resonance frequencies range | Hz | 10 to 60 |
| 8. | Percentage variation in reactance after fatigue test in comparison with that . before fatigue test | % | +/-40 (Maximum) |
| 9. | Percentage variation in power dissipation after fatigue test in comparison with that before fatigue test | % | +/-40 (Maximum) |

| Suspension Clamp for 7/3.66 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Material of components |  |  |
|  | (a) Shackle |  | Forged Steel |
|  | (b) Clamp Body & Keeper |  | Malleable cast iron / SGI |
|  | (c) U- Bolt |  | Mild Steel |
| 2. | Total Drop (Maximum) | mm | 150 |
| 3. | Breaking Strength (Minimum) | kN | 25 |
| 4. | Slipping Strength | kN | 12 to 17 |
| 5. | Galvanising |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |

| Tension Clamp for 7/3.66 mm GS Earthwire |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. |  | Description | Unit |  | Particulars/ Value |  |  |  |
| 1. | Material of components |  |  |  |  |  |  |  |
|  | (i) Anchor Shackle |  |  |  | Forged Steel |  |  |  |
|  | (ii) Compression Clamp |  |  |  |  |  |  |  |
|  | a) Steel Sleeve |  |  |  | Mild Steel |  |  |  |
|  | b) Aluminium sleeve |  |  |  | Aluminium of purity 99.5% |  |  |  |
|  | c) Aluminium Filler sleeve |  |  |  | Aluminium of purity 99.5% |  |  |  |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) |  | BHN |  | 120-200 |  |  |  |
| 3. | Dimension of sleeve Before compression |  |  |  |  |  |  |  |
|  |  |  |  | Aluminium Sleeve |  | Steel Sleeve |  | Alu filler sleeve |
| i) | Inside diameter |  | mm | 22.00 ± 0.5 |  | 11.50 ± 0.2 |  | 11.50 ± 0.2 |
| ii) | Outside diameter |  | mm | 30.00 ± 0.5 |  | 21.00 ± 0.5 |  | 21.00 ± 0.5 |
| iii) | Length |  | mm | 245 ± 5 |  | 205 ± 5 |  | 25 .0 |
| 4. | Dimensions of Sleeve after compression |  |  |  |  |  |  |  |
|  |  |  |  | Aluminium Sleeve |  |  | Steel Sleeve |  |
| i) | Outside dimension(Corner to Corner) |  | mm | 29.40 ± 0.5 |  |  | 20.20 ± 0.5 |  |
| ii) | Outside dimension (face to face) |  | mm | 25.00 ± 0.5 |  |  | 17.50 ± 0.5 |  |
| 5. | Slip strength |  | KN | 65 |  |  |  |  |
| 6. | Minimum Breaking strength of assembly (excluding clamp) |  | KN | 70 |  |  |  |  |
| 7. | Compression Pressure |  | Ton | 100 |  |  |  |  |
| 8. | Galvanising |  |  |  |  |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts |  | gm/m2 | 600 |  |  |  |  |
| b) | Purity of Zinc used for galvanising |  | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |  |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) |  | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |  |  |  |

D) 220 kV Transmission Line with  ACSR ZEBRA conductor

| 1. Suspension hardware fittings for ACSR ZEBRA Conductor |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |  |  |
|  |  |  | Single “I” Suspension Fittings with |  | Double “I” Suspension Fittings with |  | Single suspension Pilot Fitting with |
|  |  |  | AGS clamp | Free Centre clamp | AGS clamp | Free Centre clamp | Envelope clamp |
| 1. | Maximum magnetic power loss of one suspension assembly at sub-conductor current of 500 amperes | Watt | 2 | 2 | 2 | 2 | 4 |
| 2. | Slipping strength of suspension assembly | KN | 16-24 | 16-24 | 16-24 | 16-24 | 16-24 |
| 3. | Particulars of standard/ AGS preformed armour rod set for suspension assembly |  |  |  |  |  |  |
|  | a) No. of rods per set | No. | 12 | 12 | 12 | 12 | NA |
|  | b) Direction of lay |  | Right hand | Right hand | Right hand | Right hand | NA |
|  | c) Overall length after fitting on conductor | mm | 2080 | 2540 | 2080 | 2540 | NA |
|  | d) Diameter of each rod | mm | 7.87 | 7.87 | 7.87 | 7.87 | NA |
|  | e) Tolerance in |  |  |  |  |  |  |
|  | i) Diameter of each rod | ±mm | 0.10 | 0.10 | 0.10 | 0.10 | NA |
|  | ii) Length of each rod | ±mm | 25 | 25 | 25 | 25 | NA |
|  | iii) Difference of length between the longest and shortest rod in a set | ±mm | 13 | 13 | 13 | 13 | NA |
|  | f) Type of Aluminium alloy used for manufacture of PA rod set |  | 6061/ 65032 | 6061/ 65032 | 6061/ 65032 | 6061/ 65032 | NA |
|  | g) Minimum UTS of each rod | Kg/mm2 | 35 | 35 | 35 | 35 | NA |
| 4. | Particulars of Elastomer (For AGS Clamp only) |  |  |  |  |  |  |
|  | a) Type of elastomer |  | Chloroprene/ Neo prene Rubber | NA | Chloroprene /Neo prene Rubber | NA | NA |
|  | b) Shore hardness of elastomer |  | 65 to 80 | NA | 65 to 80 | NA | NA |
|  | c) Temperature range for which elastomer is designed |  | Upto 95o C | NA | Upto 95o C | NA | NA |
|  | d) Moulded on insert |  | Yes | NA | Yes | NA | NA |
| 5. | Mechanical strength of suspension fitting(excluding suspension clamp) | KN | 70 |  | 2 x 70 |  | 70 |
| 6. | Mechanical strength of suspension clamp | KN | 70 |  | 70 |  | 70 |
| 7. | Galvanising |  |  |  |  |  |  |
| a) | Weight of Zinc coating for steel parts | gm/m2 | 600 |  |  |  |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209: 1992) or 98.5 (IS 13229:1991) |  |  |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |  |  |  |

| 2. Tension hardware fittings for ACSR ZEBRA Conductor |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |
|  |  |  | Single Tension | Double Tension |
| 1. | Mechanical strength of Tension fitting(excluding dead end clamp) | KN | 120 | 2x120 |
| 2. | Type of dead end assembly |  | Compression |  |
| 3. | Compression pressure | MT | 100 |  |
| 4. | Maximum electrical resistance of dead end assembly as a percentage of equivalent length of Conductor | % | 75 |  |
| 5. | Slip strength of dead end assembly | KN | 123.80 |  |
| 6. | Galvanising |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |

E. Accessories for ACSR ZEBRA conductor for 220 kV transmission line

| 1. Mid span compression Joint for ACSR ZEBRA Conductor |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |
|  |  |  | Aluminium Sleeve | Steel Sleeve |
| 1. | Material of Joint |  | Aluminium of minimum purity 99.5% | Mild Steel(Fe-410, IS:2062) |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) | BHN | From 100 to 200 |  |
| 3. | Dimension of sleeve Before compression |  | Aluminum sleeve | Steel sleeve |
| i) | Inside diameter | mm | 31.00 ± 0.5 | 10.00 ± 0.2 |
| ii) | Outside diameter | mm | 48.00 ± 1.0 | 20.00 ± 0.5 |
| iii) | Length | mm | 710 ± 5 | 241 ± 5 |
| 4. | Dimensions of Sleeve after compression |  | Aluminum sleeve | Steel sleeve |
| i) | Outside dimension(Corner to corner) | mm | 47.00 ± 0.5 | 19.00 ± 0.5 |
| ii) | Outside dimension ( face to face) | mm | 41.00 ± 0.5 | 16.00 ± 0.5 |
| 5. | Slip strength | KN | 123.8 |  |
| 6. | Maximum resistance of the compressed unit expressed, as percentage of the resistance of equivalent length of bare conductor. | % | 75 |  |
| 7. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 154 |  |
| 8. | Maximum Radio Interference Voltage at 1 MHz for phase to earth voltage of 154 kV (rms) under dry condition | Micro Volts | 1000 |  |
| 9. | Galvanising |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |

| 2. Repair sleeve for ACSR ZEBRA Conductor |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Material |  | Aluminium of minimum purity 99.5% |
| 2. | Dimension of Aluminum sleeve Before compression |  |  |
| i) | Inside diameter | mm | 31.00 ± 0.5 |
| ii) | Outside diameter | mm | 48.00 ± 1.0 |
| iii) | Length | mm | 275.00 ± 5.0 |
| 3. | Dimensions of Aluminum Sleeve after compression |  |  |
| i) | Outside dimension(Corner to corner) | mm | 47.00 ± 0.5 |
| ii) | Outside dimension (face to face) | mm | 41.00 ± 0.5 |
| 4. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 154 |
| 5. | Maximum Radio Interference Voltage at 1 MHz for phase to earth voltage of 154 kV (rms) under dry condition | Micro Volts | 1000 |

| 3. Vibration Damper for ACSR ZEBRA Conductor |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Type of Damper |  | 4R-Stockbridge type |
| 2. | Materials of components |  |  |
|  | a) Damper masses |  | Cast iron/ mild steel hot dip galvanised / Zinc alloy |
|  | b) Clamp |  | Aluminum alloy 4600 |
|  | c) Messenger cable |  | High tensile strength galvanized steel |
| 3. | Number of strands in stranded messenger cable | Nos. | 19 |
| 4. | Minimum ultimate tensile strength of stranded messenger cable | Kg/mm2 | 135 |
| 5. | Slip strength of stranded messenger cable (mass pull off) | KN | 5 |
| 6. | Slipping strength of damper clamp |  |  |
|  | (a) Before fatigue test | KN | 2.5 |
|  | (b) After fatigue test | KN | 2 |
| 7. | Resonance frequencies range | Hz | 5 to 45 |
| 8. | Maximum magnetic power loss per vibration damper watts for 500 amps, 50 Hz Alternating Current | Watts | 1 |
| 9. | Minimum corona Extinction voltage kV (rms) under dry condition | kV | 154 |
| 10. | Maximum Radio Interference Voltage (RIV) at 1 MHz for phase to earth voltage of 154 kV (rms) under dry condition | Micro Volts | 1000 |
| 11. | Percentage variation in reactance after fatigue test in comparison with that . before fatigue test | % | +/-40 (Maximum) |
| 12. | Percentage variation in power dissipation after fatigue test in comparison with that before fatigue test | % | +/-40 (Maximum) |
| 13. | Galvanising |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |

F. Accessories for 7/3.15 mm GS Earthwire for 220 kV and 132 kV transmission line

| 1. Mid span compression Joint for 7/3.15 mm GS Earthwire |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |  |
|  |  |  | Aluminium / Filler Sleeve |  | Steel Sleeve |  |
| 1. | Material of Joint |  | Aluminium of minimum purity 99.5% |  | Mild Steel(Fe-410, IS:2062) |  |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) | BHN | From 100 to 200 |  |  |  |
| 3. | Dimension of sleeve Before compression |  |  |  |  |  |
|  |  |  | Aluminium Sleeve | Steel Sleeve |  | Alu filler sleeve |
| i) | Inside diameter | mm | 22.00 ± 0.5 | 10.00 ± 0.2 |  | 11.50 ± 0.2 |
| ii) | Outside diameter | mm | 30.00 ± 0.5 | 21.00 ± 0.5 |  | 21.00 ± 0.5 |
| iii) | Length | mm | 315 ± 5 | 230 ± 5 |  | 25 ± 2 |
| 4. | Dimensions of Sleeve after compression |  |  |  |  |  |
|  |  |  | Aluminium Sleeve |  | Steel Sleeve |  |
| i) | Outside dimension(Corner to Corner) | mm | 29.40 ± 0.5 |  | 20.20 ± 0.5 |  |
| ii) | Outside dimension (face to face) | mm | 25.00 ± 0.5 |  | 17.50 ± 0.5 |  |
| 5. | Slip strength | KN | 53.20 |  |  |  |
| 6. | Maximum resistance of the compressed unit expressed, as percentage of the resistance of equivalent length of bare Earthwire | % | 75 |  |  |  |
| 7. | Galvanising |  |  |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |  |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |  |  |

| 2. Flexible Copper Bond for 7/3.15 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Stranding |  | 19 (12+6+1) / dia 2.54 |
| 2. | Cross sectional area | Sq.mm | 95 |
| 3. | Minimum copper equivalent area | Sq.mm | 750 + 5 |
| 4. | Length of copper cable | mm | Aluminium alloy |
| 5. | Material of lugs |  | 19 (12+6+1) / dia 2.54 |
| 6. | Bolt Size |  |  |
|  | i) Diameter | mm | 16 |
|  | ii) Length | mm | 40 |

| 3. Vibration Damper for 7/3.15 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Type of Damper |  | 4R-Stockbridge type |
| 2. | Materials of components |  |  |
|  | a) Damper masses |  | Cast iron/ mild steel hot dip galvanised / Zinc alloy |
|  | b) Clamp |  | Aluminum alloy 4600 |
|  | c) Messenger cable |  | High tensile strength galvanized steel |
| 3. | Number of strands in stranded messenger cable | Nos. | 19 |
| 4. | Minimum ultimate tensile strength of stranded messenger cable | Kg/mm2 | 135 |
| 5. | Slip strength of stranded messenger cable (mass pull off) | kN | 2.5 |
| 6. | Slipping strength of damper clamp |  |  |
|  | (a) Before fatigue test | kN | 2.5 |
|  | (b) After fatigue test | kN | 2 |
| 7. | Resonance frequencies range | Hz | 10 to 60 |
| 8. | Percentage variation in reactance after fatigue test in comparison with that . before fatigue test | % | +/-40 (Maximum) |
| 9. | Percentage variation in power dissipation after fatigue test in comparison with that before fatigue test | % | +/-40 (Maximum) |
| 10. | Galvanising |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |

| 4. Suspension Clamp for 7/3.15 mm GS Earthwire |  |  |  |
| --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |
| 1. | Material of components |  |  |
|  | (a) Shackle |  | Forged Steel |
|  | (b) Clamp Body & Keeper |  | Malleable cast iron / SGI |
|  | (c) U- Bolt |  | Mild Steel (Fe 410, IS 2062) |
| 2. | Total Drop (Maximum) | mm | 150 |
| 3. | Breaking Strength (Minimum) | kN | 25 |
| 4. | Slipping Strength | kN | 9 to 14 |
| 5. | Galvanising |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |

| 5. Tension Clamp for 7/3.15 mm GS Earthwire |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl. | Description | Unit | Particulars/ Value |  |  |  |
| 1. | Material of components |  |  |  |  |  |
|  | (i) Anchor Shackle |  | Forged Steel |  |  |  |
|  | (ii) Compression Clamp |  |  |  |  |  |
|  | a) Steel Sleeve |  | Mild Steel (Fe 410, IS 2062) |  |  |  |
|  | b) Aluminium sleeve |  | Aluminium of purity 99.5% |  |  |  |
|  | c) Aluminium Filler sleeve |  | Aluminium of purity 99.5% |  |  |  |
| 2. | Range of Hardness of the steel sleeve (Brinnel hardness) | BHN | 100-200 |  |  |  |
| 3. | Dimension of sleeve Before compression |  |  |  |  |  |
|  |  |  | Aluminium Sleeve | Steel Sleeve |  | Alu filler sleeve |
| i) | Inside diameter | mm | 22.00 ± 0.5 | 10.00 ± 0.2 |  | 11.50 ± 0.2 |
| ii) | Outside diameter | mm | 30.00 ± 0.5 | 21.00 ± 0.5 |  | 21.00 ± 0.5 |
| iii) | Length | mm | 220 ± 5 | 180 ± 5 |  | 25 .0+2 |
| 4. | Dimensions of Sleeve after compression |  |  |  |  |  |
|  |  |  | Aluminium Sleeve |  | Steel Sleeve |  |
| i) | Outside dimension(Corner to Corner) | mm | 29.40 ± 0.5 |  | 20.20 ± 0.5 |  |
| ii) | Outside dimension (face to face) | mm | 25.00 ± 0.5 |  | 17.50 ± 0.5 |  |
| 5. | Slip strength | KN | 53.20 |  |  |  |
| 6. | Minimum Breaking strength of assembly (excluding clamp) | KN | 70 |  |  |  |
| 7. | Compression Pressure | Ton | 100 |  |  |  |
| 8. | Galvanising |  |  |  |  |  |
| a) | Minimum weight of Zinc coating for steel parts | gm/m2 | 600 |  |  |  |
| b) | Purity of Zinc used for galvanising | % | 99.95 (IS 209) or 98.5 (IS 13229) |  |  |  |
| c) | Min. No. of dips in standard preece test the ferrous parts can withstand (wherever applicable) | No. | a) Fasteners: 4 dips of 1 minute b) Spring washers: 3 dips of 1 minute & c) all others: 6 dips of 1 minute |  |  |  |